## README
THIS IS AN OPEN SOURCED MANUAL J LOAD CALCULATION TOOL. I PUT THIS TOGETHER WITH NO PRIOR KNOWLEDGE OF EXCEL SO IF THERE ARE BUGS YOU WILL BE ABLE TO FIX
TO DO
BETTER AND MORE UNIFORM TEMPLATING
COLOR CODE TO DESCRIBE FIELD TYPE
BUILD CONSTRUCTION DETAILS LIST TO DROP DOWN FOR HTM
MAKE THE CONSTRUCTION CELLS SHOW THE CONSTRUCTION NUMBER AFTER THE SELECTION HAS BEEN MADE, INSTEAD OF THE COMPLETE DESCRIPTION
https://www.automateexcel.com/vba/auto-open-macro/-will open a program window instead of a spreadsheet--this

## CALC PROCEDURES A,B,C,D
PROCEDURE A – WINTER INFILTRATION HTM CALCULATION
1	WINTER INFILTRATION CFM
			AC/HR	X	CU. FT	X	0.0167	=	CFM
	WINTER INFILTRATION BTUH
		1.1	X		CFM	X		WINTER TD	=	BTUH

	WINTER INFILTRATION HTM
			BTUH	/		TOTAL WINDOW & DOOR AREA	=		HTM

PROCEDURE B – SUMMER INFILTRATION HTM CALCULATION
		SUMMER INFILTRATION CFM
			AC/HR	X		CU. FT.	X	0.0167	=		BTUH
		SUMMER INFILTRATION BTUH
		1.1	X		CFM	X		SUMMER TD	=		BTUH
		SUMMER INFILTRATION HTM
			BTUH	/		TOTAL WINDOW & DOOR AREA		HTM

PROCEDURE C – LATENT INFILTRATION GAIN
		0.068	X		GR. DIFF.	X		SUMMER CFM	=		BTUH

PROCEDURE D – EQUIPMENT SIZING LOADS

		SENSIBLE SIZING LOAD
		SENSIBLE VENTILATION LOAD
		1.1	X		VENT. CFM	X		SUMMER TD	=		BTUH
		SENSIBLE LOAD FOR STRUCTURE (LINE 19)	+		BTUH
		SUM OF VENTILATION AND STRUCTURE LOADS
		RATING & TEMPERATURE SWING MULTIPLIER	X		RSM
		EQUIPMENT SIZING LOAD – SENSIBLE	=		BTUH

		LATENT SIZING LOAD

		LATENT VENTILATION LOAD
		0.68	X		VENT. CFM	X		GR. DIFF.
		INTERNAL LOADS	=	230	X		NUMBER OF PEOPLE
		INFILTRATION LOAD FROM PROCEDURE C	+		BTUH
		EQUIPTMENT SIZING LOAD – LATENT	=		BTUH

## CONSTRUCTIONDETAILS
1	NAME OF ROOM					ENTIRE HOUSE	Room A
2	RUNNING FT EXPOSED WALL
3	ROOM DIMENSIONS, FT
3A	ROOM AREA, SQ FT					#VALUE!	0			0
4	CEILING HT, FT		DIRECTIONS ROOM FACE				8
TYPE OF EXPOSURE			CONST. NO.		HTM		AREA OR LENGTH	AREA OR LENGTH	BTUH		AREA OR LENGTH	BTUH
				HTG	CLG			HTG	CLG		HTG	CLG
5	GROSS EXPOSED WALLS AND PARTITIONS	A
		B
		C
		D
6	WINDOWS AND GLASS DOORS (HEATING)	A
		B
		C
		D
7	WINDOWS AND GLASS DOORS (COOLING)	NORTH
		E & W OR NE & NW
		SOUTH OR SE & SW

	OTHER
8	OTHER DOORS
9	NET EXPOSED WALLS AND PARTITIONS	A
		B
		C
		D
10	CEILINGS	A
		B
11	FLOORS	A
		B
12	INFILTRATION HTM
13	SUB TOT. BTUH LOSS = 6+8+9+10+11+12
14	DUCT BTUH LOSS				%
15	TOTAL BTUH LOSS = 13+14
16	PEOPLE @ 300 AND APPLIANCES @ 1200
17	SENSIBLE BTUH GAIN = 7+8+9+10+11+12+16
18	DUCT BTUH GAIN					%
19	TOTAL SENSIBLE GAIN = 17+18

## TABLE 1
TABLE 1
	WINTER DESIGN TEMP 70-72				SUMMER DESIGN TEMP 75
WINTER					SUMMER
LOCATION	LATITUDE DEGREES	97 ½% DESIGN DB	HEATING D.D. BELOW 65°F	DESIGN TEMP DIFF	2 ½% DESIGN DB	COINCIDENT DESIGN WB	GRAINS DIFF 55% RH	GRAINS DIFFERENCE 50% RH	DAILY RANGE	DESIGN TEMP DIFF
OMAHA	441	-3	6290	75	91	75	35	42	22 M	15
LINCOLN	40	-2	6050	75	95	74	21	28	24 M	20

## TABLE 2
TABLE 2
HEAT TRANSFER MULTIPLIERS (HEATING)
NO. 1	SINGLE PANE WINDOW	WINTER TEMP DIFFERENCE
		20	25	30	35	40	45	50	55	60	65	70	75	80	85	90	95	U
CLEAR GLASS
A.	WOOD FRAME	19.8	24.8	29.7	34.7	39.6	44.6	49.5	54.5	59.4	64.4	69.3	74.3	79.2	84.2	89.1	94.1	.990
B.	T.I.M. FRAME	20.9	26.1	31.4	36.6	41.8	47.0	52.3	57.5	62.7	67.9	73.2	78.4	83.6	88.8	94.1	99.3	1.045
C.	METAL FRAME	23.1	28.9	34.7	40.4	46.2	52.0	57.8	63.5	69.3	75.1	80.9	86.6	92.4	98.2	104.0	109.7	1.155
LOW EMITTANCE GLASS, E = 0.60
D.	WOOD FRAME	18.4	23.0	27.5	32.1	36.7	41.3	45.9	50.5	55.1	59.7	64.3	68.9	73.4	78.0	82.6	87.2	.918
E.	T.I.M. FRAME	19.4	24.2	29.1	33.9	38.8	43.6	48.5	53.3	58.1	63.0	67.8	72.7	77.5	82.4	87.2	92.1	.969
F.	METAL FRAME	21.4	26.8	32.1	37.5	42.8	48.2	53.6	58.9	64.3	69.6	75.0	80.3	85.7	91.0	96.4	101.7	1.071
LOW EMITTANCE GLASS, E = 0.40
G.	WOOD FRAME	16.4	20.5	24.6	28.7	32.8	36.9	41.0	45.0	49.1	53.2	57.3	61.4	65.5	69.6	73.7	77.8	.819
H.	T.I.M. FRAME	17.3	21.6	26.0	30.3	34.6	38.9	43.3	47.6	51.9	56.2	60.6	64.9	69.2	73.5	77.9	82.2	.865
I.	METAL FRAME	19.1	23.9	28.7	33.5	38.2	43.0	47.8	52.6	57.4	62.1	66.9	71.7	76.5	81.3	86.0	90.8	.956
LOW EMITTANCE GLASS, E = 0.20
J.	WOOD FRAME	14.2	17.8	21.3	24.9	28.4	32.0	35.6	39.1	42.7	46.2	49.8	53.3	56.9	60.4	64.0	67.5	.711
K.	T.I.M. FRAME	15.0	18.8	22.5	26.3	30.0	33.8	37.6	41.3	45.1	48.8	52.6	56.3	60.1	63.8	67.6	71.3	.751
L.	METAL FRAME	16.6	20.8	24.9	29.1	33.2	37.4	41.5	45.7	49.8	54.0	58.1	62.3	66.4	70.6	74.7	78.9	.830
NO. 2	SINGLE PANE WINDOW & STORM	WINTER TEMP DIFFERENCE
		20	25	30	35	40	45	50	55	60	65	70	75	80	85	90	95	U
CLEAR GLASS
A.	WOOD FRAME	09.5	11.9	14.3	16.6	19.0	21.4	23.8	26.1	28.5	30.9	33.3	35.6	38.0	40.4	42.8	45.1	.475
B.	T.I.M. FRAME	10.5	13.1	15.8	18.4	21.0	23.6	26.3	28.9	31.5	34.1	36.8	39.4	42.0	44.6	47.3	49.9	.525
C.	METAL FRAME	13.0	16.3	19.5	22.8	26.0	29.3	32.5	35.8	39.0	42.3	45.5	48.8	52.0	55.3	58.5	61.8	.650
LOW EMITTANCE GLASS
D.	WOOD FRAME	08.4	10.5	12.5	14.6	16.7	18.8	20.9	23.0	25.1	27.2	29.3	31.4	33.4	35.5	37.6	39.7	.418
E.	T.I.M. FRAME	09.2	11.6	13.9	16.2	18.5	20.8	23.1	25.4	27.7	30.0	32.3	34.7	37.0	39.3	41.6	43.9	.462
F.	METAL FRAME	11.4	14.3	17.2	20.0	22.9	25.7	28.6	31.5	34.3	37.2	40.0	42.9	45.8	48.6	51.5	54.3	.572
NO. 3	DOUBLE PANE WINDOW	WINTER TEMP DIFFERENCE
		20	25	30	35	40	45	50	55	60	65	70	75	80	85	90	95	U
CLEAR GLASS
A.	WOOD FRAME	11.0	13.8	16.5	19.3	22.0	24.8	27.6	30.3	33.1	35.8	38.6	41.3	44.1	46.8	49.6	52.3	.551
B.	T.I.M. FRAME	12.2	15.2	18.3	21.3	24.4	27.4	30.5	33.5	36.5	39.6	42.6	45.7	48.7	51.8	54.8	57.9	.609
C.	METAL FRAME	14.5	18.1	21.8	25.4	29.0	32.6	36.3	39.9	43.5	47.1	50.8	54.4	58.0	61.6	65.3	68.9	.725
LOW EMITTANCE GLASS
D.	WOOD FRAME	07.2	09.0	10.8	12.6	14.4	16.2	18.1	19.9	21.7	23.5	25.3	27.1	28.9	30.7	32.5	34.3	.361
E.	T.I.M. FRAME	08.0	10.0	12.0	14.0	16.0	18.0	20.0	21.9	23.9	25.9	27.9	29.9	31.9	33.9	35.9	37.9	.399
F.	METAL FRAME	09.5	11.9	14.3	16.6	19.0	21.4	23.8	26.1	28.5	30.9	33.3	35.6	38.0	40.4	42.8	45.1	.475
ADJUSTABLE BLIND BETWEEN PANES
G.	WOOD FRAME	04.8	06.0	07.1	08.3	09.5	10.7	11.9	13.1	14.3	15.5	16.7	17.9	19.0	20.2	21.4	22.6	.238
H.	T.I.M. FRAME	05.3	06.6	07.9	09.2	10.5	11.8	13.2	14.5	15.8	17.1	18.4	19.7	21.0	22.4	23.7	25.0	.263
NO. 4	DOUBLE PANE WINDOW & STORM	WINTER TEMP DIFFERENCE
		20	25	30	35	40	45	50	55	60	65	70	75	80	85	90	95	U
A.	WOOD FRAME	06.8	08.5	10.2	11.9	13.6	15.3	17.1	18.8	20.5	22.2	23.9	25.6	27.3	29.0	30.7	32.4	.341
B.	T.I.M. FRAME	07.7	09.6	11.6	13.5	15.4	17.3	19.3	21.2	23.1	25.0	27.0	28.9	30.8	32.7	34.7	36.6	.385
C.	METAL FRAME	09.8	12.3	14.7	17.2	19.6	22.1	24.5	27.0	29.4	31.9	34.3	36.8	39.2	41.7	44.1	46.6	.490
LOW EMITTANCE GLASS		00.0	00.0	00.0	00.0	00.0	00.0	00.0	00.0	00.0	00.0	00.0	00.0	00.0	00.0	00.0	00.0
D.	WOOD FRAME	05.3	06.6	07.9	09.2	10.5	11.8	13.2	14.5	15.8	17.1	18.4	19.7	21.0	22.4	23.7	25.0	.263
E.	T.I.M. FRAME	05.9	07.4	08.9	10.4	11.9	13.4	14.9	16.3	17.8	19.3	20.8	22.3	23.8	25.2	26.7	28.2	.297
F.	METAL FRAME	07.6	09.5	11.3	13.2	15.1	17.0	18.9	20.8	22.7	24.6	26.5	28.4	30.2	32.1	34.0	35.9	.378

NO. 5	TRIPLE PANE WINDOWS	WINTER TEMP DIFFERENCE
		20	25	30	35	40	45	50	55	60	65	70	75	80	85	90	95	U
CLEAR GLASS
A.	WOOD FRAME	07.6	09.5	11.4	13.3	15.2	17.1	19.0	20.9	22.8	24.7	26.6	28.5	30.4	32.3	34.2	36.1	.380
B.	T.I.M. FRAME	08.8	11.0	13.2	15.4	17.6	19.8	22.0	24.1	26.3	28.5	30.7	32.9	35.1	37.3	39.5	41.7	.439
C.	METAL FRAME	10.9	13.7	16.4	19.1	21.8	24.6	27.3	30.0	32.8	35.5	38.2	41.0	43.7	46.4	49.1	51.9	.546
LOW EMITTANCE GLASS
D.	WOOD FRAME	06.2	07.8	09.4	10.9	12.5	14.0	15.6	17.2	18.7	20.3	21.8	23.4	25.0	26.5	28.1	29.6	.312
E.	T.I.M. FRAME	07.2	09.0	10.8	12.6	14.4	16.2	18.0	19.8	21.6	23.4	25.2	27.0	28.8	30.6	32.4	34.2	.360
F.	METAL FRAME	09.0	11.2	13.4	15.7	17.9	20.2	22.4	24.6	26.9	29.1	31.4	33.6	35.8	38.1	40.3	42.6	.448
CLEAR GLASS & STORM
G.	WOOD FRAME	05.3	06.6	07.9	09.2	10.5	11.8	13.2	14.5	15.8	17.1	18.4	19.7	21.0	22.4	23.7	25.0	.263
H.	T.I.M. FRAME	06.2	07.8	09.3	10.9	12.4	14.0	15.6	17.1	18.7	20.2	21.8	23.3	24.9	26.4	28.0	29.5	.311
I.	METAL FRAME	07.6	09.5	11.3	13.2	15.1	17.0	18.9	20.8	22.7	24.6	26.5	28.4	30.2	32.1	34.0	35.9	.378
NO. 6	JALOUSIE WINDOWS	WINTER TEMP DIFFERENCE
		20	25	30	35	40	45	50	55	60	65	70	75	80	85	90	95	U
A.	METAL FRAME-SINGLE GLASS	22.0	27.5	33.0	38.5	44.0	49.5	55.0	60.5	66.0	71.5	77.0	82.5	88.0	93.5	99.0	104.5	1.100
B.	METAL FRAME-SINGLE GLASS & STORM	10.0	12.5	15.0	17.5	20.0	22.5	25.0	27.5	30.0	32.5	35.0	37.5	40.0	42.5	45.0	47.5	.500
NO. 7	SKYLIGHTS	WINTER TEMP DIFFERENCE
		20	25	30	35	40	45	50	55	60	65	70	75	80	85	90	95	U
SINGLE; CLEAR GLASS
A.	WOOD FRAME	22.1	27.7	33.2	38.7	44.3	49.8	55.4	60.9	66.4	72.0	77.5	83.0	88.6	94.1	99.6	105.2	1.107
B.	T.I.M. FRAME	23.4	29.2	35.1	40.9	46.8	52.6	58.5	64.3	70.1	76.0	81.8	87.7	93.5	99.4	105.2	111.1	1.169
C.	METAL FRAME	25.8	32.3	38.8	45.2	51.7	58.1	64.6	71.1	77.5	84.0	90.4	96.9	103.4	109.8	116.3	122.7	1.292
SINGLE; PLASTIC DOME
D.	WOOD FRAME	20.7	25.9	31.1	36.2	41.4	46.6	51.8	56.9	62.1	67.3	72.5	77.6	82.8	88.0	93.2	98.3	1.035
E.	T.I.M. FRAME	21.9	27.3	32.8	38.3	43.7	49.2	54.7	60.1	65.6	71.0	76.5	82.0	87.4	92.9	98.4	103.8	1.093
F.	METAL FRAME	24.2	30.2	36.2	42.3	48.3	54.4	60.4	66.4	72.5	78.5	84.6	90.6	96.6	102.7	108.7	114.8	1.208
DOUBLE; PLASTIC DOME OR CLEAR GLASS
G.	WOOD FRAME	13.3	16.6	20.0	23.3	26.6	29.9	33.3	36.6	39.9	43.2	46.6	49.9	53.2	56.5	59.9	63.2	.665
H.	T.I.M. FRAME	14.7	18.4	22.1	25.7	29.4	33.1	36.8	40.4	44.1	47.8	51.5	55.1	58.8	62.5	66.2	69.8	.735
I.	METAL FRAME	17.5	21.9	26.3	30.6	35.0	39.4	43.8	48.1	52.5	56.9	61.3	65.6	70.0	74.4	78.8	83.1	.875
DOUBLE; LOW EMITTANCE GLASS
J.	WOOD FRAME	09.9	12.4	14.8	17.3	19.8	22.2	24.7	27.2	29.6	32.1	34.6	37.1	39.5	42.0	44.5	46.9	.494
K.	T.I.M. FRAME	10.9	13.7	16.4	19.1	21.8	24.6	27.3	30.0	32.8	35.5	38.2	41.0	43.7	46.4	49.1	51.9	.546
L.	METAL FRAME	13.0	16.3	19.5	22.8	26.0	29.3	32.5	35.8	39.0	42.3	45.5	48.8	52.0	55.3	58.5	61.8	.650
NO. 8	SLIDING GLASS DOORS	WINTER TEMP DIFFERENCE
		20	25	30	35	40	45	50	55	60	65	70	75	80	85	90	95	U
SINGLE PANE; CLEAR GLASS
A.	WOOD FRAME	19.8	24.8	29.7	34.7	39.6	44.6	49.5	54.5	59.4	64.4	69.3	74.3	79.2	84.2	89.1	94.1	.990
B.	T.I.M. FRAME	20.9	26.1	31.4	36.6	41.8	47.0	52.3	57.5	62.7	67.9	73.2	78.4	83.6	88.8	94.1	99.3	1.045
C.	METAL FRAME	23.1	28.9	34.7	40.4	46.2	52.0	57.8	63.5	69.3	75.1	80.9	86.6	92.4	98.2	104.0	109.7	1.155
SINGLE PANE LOW E GLASS
D.	WOOD FRAME	16.4	20.5	24.6	28.7	32.8	36.9	41.0	45.0	49.1	53.2	57.3	61.4	65.5	69.6	73.7	77.8	.819
E.	T.I.M. FRAME	17.3	21.6	26.0	30.3	34.6	38.9	43.3	47.6	51.9	56.2	60.6	64.9	69.2	73.5	77.9	82.2	.865
F.	METAL FRAME	19.1	23.9	28.7	33.5	38.2	43.0	47.8	52.6	57.4	62.1	66.9	71.7	76.5	81.3	86.0	90.8	.956
SINGLE PANE & STORM, CLEAR GLASS
G.	WOOD FRAME	09.5	11.9	14.3	16.6	19.0	21.4	23.8	26.1	28.5	30.9	33.3	35.6	38.0	40.4	42.8	45.1	.475
H.	T.I.M. FRAME	10.5	13.1	15.8	18.4	21.0	23.6	26.3	28.9	31.5	34.1	36.8	39.4	42.0	44.6	47.3	49.9	.525
I.	METAL FRAME	13.0	16.3	19.5	22.8	26.0	29.3	32.5	35.8	39.0	42.3	45.5	48.8	52.0	55.3	58.5	61.8	.650
SINGLE PANE & STORM, LOW E GLASS
J.	WOOD FRAME	08.4	10.5	12.5	14.6	16.7	18.8	20.9	23.0	25.1	27.2	29.3	31.4	33.4	35.5	37.6	39.7	.418
K.	T.I.M. FRAME	09.2	11.6	13.9	16.2	18.5	20.8	23.1	25.4	27.7	30.0	32.3	34.7	37.0	39.3	41.6	43.9	.462
L.	METAL FRAME	11.4	14.3	17.2	20.0	22.9	25.7	28.6	31.5	34.3	37.2	40.0	42.9	45.8	48.6	51.5	54.3	.572
DOUBLE PANE, CLEAR GLASS
M.	WOOD FRAME	11.0	13.8	16.5	19.3	22.0	24.8	27.6	30.3	33.1	35.8	38.6	41.3	44.1	46.8	49.6	52.3	.551
N.	T.I.M. FRAME	12.2	15.2	18.3	21.3	24.4	27.4	30.5	33.5	36.5	39.6	42.6	45.7	48.7	51.8	54.8	57.9	.609
O.	METAL FRAME	14.5	18.1	21.8	25.4	29.0	32.6	36.3	39.9	43.5	47.1	50.8	54.4	58.0	61.6	65.3	68.9	.725
DOUBLE PANE, LOW E GLASS
P.	WOOD FRAME	07.2	09.0	10.8	12.6	14.4	16.2	18.1	19.9	21.7	23.5	25.3	27.1	28.9	30.7	32.5	34.3	.361
Q.	T.I.M. FRAME	08.0	10.0	12.0	14.0	16.0	18.0	20.0	21.9	23.9	25.9	27.9	29.9	31.9	33.9	35.9	37.9	.399
R.	METAL FRAME	09.5	11.9	14.3	16.6	19.0	21.4	23.8	26.1	28.5	30.9	33.3	35.6	38.0	40.4	42.8	45.1	.475
TRIPLE PANE OR DOUBLE PANE & STORM
S.	WOOD FRAME	06.8	08.5	10.2	11.9	13.6	15.3	17.1	18.8	20.5	22.2	23.9	25.6	27.3	29.0	30.7	32.4	.341
T.	T.I.M. FRAME	07.7	09.6	11.6	13.5	15.4	17.3	19.3	21.2	23.1	25.0	27.0	28.9	30.8	32.7	34.7	36.6	.385
U.	METAL FRAME	09.8	12.3	14.7	17.2	19.6	22.1	24.5	27.0	29.4	31.9	34.3	36.8	39.2	41.7	44.1	46.6	.490
TRIPLE OR DOUBLE & STORM ,LOW E
V.	WOOD FRAME	05.3	06.6	07.9	09.2	10.5	11.8	13.2	14.5	15.8	17.1	18.4	19.7	21.0	22.4	23.7	25.0	.263
W.	T.I.M. FRAME	05.9	07.4	08.9	10.4	11.9	13.4	14.9	16.3	17.8	19.3	20.8	22.3	23.8	25.2	26.7	28.2	.297
X.	METAL FRAME	07.6	09.5	11.3	13.2	15.1	17.0	18.9	20.8	22.7	24.6	26.5	28.4	30.2	32.1	34.0	35.9	.378
NO. 9	FRENCH DOORS	WINTER TEMP DIFFERENCE
		20	25	30	35	40	45	50	55	60	65	70	75	80	85	90	95	U
SINGLE PANE, CLEAR GLASS
A.	WOOD FRAME	18.7	23.4	28.1	32.7	37.4	42.1	46.8	51.4	56.1	60.8	65.5	70.1	74.8	79.5	84.2	88.8	.935
B.	T.I.M. FRAME	19.8	24.8	29.7	34.7	39.6	44.6	49.5	54.5	59.4	64.4	69.3	74.3	79.2	84.2	89.1	94.1	.990
C.	METAL FRAME	24.2	30.3	36.3	42.4	48.4	54.5	60.5	66.6	72.6	78.7	84.7	90.8	96.8	102.9	108.9	115.0	1.210
SINGLE PANE, LOW E GLASS
D.	WOOD FRAME	15.5	19.4	23.2	27.1	31.0	34.8	38.7	42.6	46.4	50.3	54.2	58.1	61.9	65.8	69.7	73.5	.774
E.	T.I.M. FRAME	16.4	20.5	24.6	28.7	32.8	36.9	41.0	45.0	49.1	53.2	57.3	61.4	65.5	69.6	73.7	77.8	.819
F.	METAL FRAME	20.0	25.0	30.0	35.0	40.0	45.0	50.1	55.1	60.1	65.1	70.1	75.1	80.1	85.1	90.1	95.1	1.001
SINGLE PANE & STORM, CLEAR GLASS
G.	WOOD FRAME	10.4	13.1	15.7	18.3	20.9	23.5	26.1	28.7	31.3	33.9	36.5	39.2	41.8	44.4	47.0	49.6	.522
H.	T.I.M. FRAME	11.0	13.8	16.5	19.3	22.0	24.8	27.6	30.3	33.1	35.8	38.6	41.3	44.1	46.8	49.6	52.3	.551
I.	METAL FRAME	15.1	18.9	22.6	26.4	30.2	33.9	37.7	41.5	45.2	49.0	52.8	56.6	60.3	64.1	67.9	71.6	.754
DOUBLE PANE, CLEAR GLASS
M.	WOOD FRAME	10.4	13.1	15.7	18.3	20.9	23.5	26.1	28.7	31.3	33.9	36.5	39.2	41.8	44.4	47.0	49.6	.522
N.	T.I.M. FRAME	11.0	13.8	16.5	19.3	22.0	24.8	27.6	30.3	33.1	35.8	38.6	41.3	44.1	46.8	49.6	52.3	.551
O.	METAL FRAME	15.1	18.9	22.6	26.4	30.2	33.9	37.7	41.5	45.2	49.0	52.8	56.6	60.3	64.1	67.9	71.6	.754
DOUBLE PANE, LOW E GLASS
P.	WOOD FRAME	06.8	08.6	10.3	12.0	13.7	15.4	17.1	18.8	20.5	22.2	23.9	25.7	27.4	29.1	30.8	32.5	.342
Q.	T.I.M. FRAME	07.2	09.0	10.8	12.6	14.4	16.2	18.1	19.9	21.7	23.5	25.3	27.1	28.9	30.7	32.5	34.3	.361
R.	METAL FRAME	09.9	12.4	14.8	17.3	19.8	22.2	24.7	27.2	29.6	32.1	34.6	37.1	39.5	42.0	44.5	46.9	.494
TRIPLE PANE, CLEAR GLASS
S.	WOOD FRAME	07.4	09.3	11.1	13.0	14.8	16.7	18.6	20.4	22.3	24.1	26.0	27.8	29.7	31.5	33.4	35.2	.371
T.	T.I.M. FRAME	07.8	09.8	11.7	13.7	15.6	17.6	19.5	21.5	23.4	25.4	27.3	29.3	31.2	33.2	35.1	37.1	.390
U.	METAL FRAME	11.7	14.6	17.6	20.5	23.4	26.3	29.3	32.2	35.1	38.0	41.0	43.9	46.8	49.7	52.7	55.6	.585
TRIPLE PANE, LOW E
V.	WOOD FRAME	05.1	06.4	07.7	09.0	10.3	11.6	12.9	14.1	15.4	16.7	18.0	19.3	20.6	21.8	23.1	24.4	.257
W.	T.I.M. FRAME	05.4	06.8	08.1	09.5	10.8	12.2	13.5	14.9	16.2	17.6	18.9	20.3	21.6	23.0	24.3	25.7	.270
X.	METAL FRAME	08.1	10.1	12.2	14.2	16.2	18.2	20.3	22.3	24.3	26.3	28.4	30.4	32.4	34.4	36.5	38.5	.405
NO. 10	WOOD DOORS	WINTER TEMP DIFFERENCE
		20	25	30	35	40	45	50	55	60	65	70	75	80	85	90	95	U
A.	HOLLOW CORE	11.2	14.0	16.8	19.6	22.4	25.2	28.0	30.8	33.6	36.4	39.2	42.0	44.8	47.6	50.4	53.2	.560
B.	HOLLOW CORE & WOOD STORM	06.6	08.3	09.9	11.6	13.2	14.9	16.5	18.2	19.8	21.5	23.1	24.8	26.4	28.1	29.7	31.4	.330
C.	HOLLOW CORE & METAL STORM	07.2	09.0	10.8	12.6	14.4	16.2	18.0	19.8	21.6	23.4	25.2	27.0	28.8	30.6	32.4	34.2	.360
D.	SOLID CORE	09.2	11.5	13.8	16.1	18.4	20.7	23.0	25.3	27.6	29.9	32.2	34.5	36.8	39.1	41.4	43.7	.460
E.	SOLID CORE & WOOD STORM	05.8	07.3	08.7	10.2	11.6	13.1	14.5	16.0	17.4	18.9	20.3	21.8	23.2	24.7	26.1	27.6	.290
F.	SOLID CORE & METAL STORM	06.4	08.0	09.6	11.2	12.8	14.4	16.0	17.6	19.2	20.8	22.4	24.0	25.6	27.2	28.8	30.4	.320
G.	PANEL	13.4	16.8	20.1	23.5	26.8	30.2	33.5	36.9	40.2	43.6	46.9	50.3	53.6	57.0	60.3	63.7	.670
H.	PANEL & WOOD STORM	07.2	09.0	10.8	12.6	14.4	16.2	18.0	19.8	21.6	23.4	25.2	27.0	28.8	30.6	32.4	34.2	.360
I.	PANEL & METAL STORM	08.2	10.3	12.3	14.4	16.4	18.5	20.5	22.6	24.6	26.7	28.7	30.8	32.8	34.9	36.9	39.0	.410
NO. 11	METAL DOORS	WINTER TEMP DIFFERENCE
		20	25	30	35	40	45	50	55	60	65	70	75	80	85	90	95	U
A.	FIBERGLASS CORE	11.8	14.8	17.7	20.7	23.6	26.6	29.5	32.5	35.4	38.4	41.3	44.3	47.2	50.2	53.1	56.1	.590
B.	FIBERGLASS CORE & STORM	07.3	09.2	11.0	12.8	14.7	16.5	18.4	20.2	22.0	23.9	25.7	27.5	29.4	31.2	33.0	34.9	.367
C.	POLYSTYRENE CORE	09.4	11.8	14.1	16.5	18.8	21.2	23.5	25.9	28.2	30.6	32.9	35.3	37.6	40.0	42.3	44.7	.470
D.	POLYSTYRENE CORE & STORM	06.3	07.9	09.5	11.1	12.7	14.3	15.9	17.4	19.0	20.6	22.2	23.8	25.4	26.9	28.5	30.1	.317
E.	URETHANE CORE	03.8	04.8	05.7	06.7	07.6	08.6	09.5	10.5	11.4	12.4	13.3	14.3	15.2	16.2	17.1	18.1	.190
F.	URETHATNE CORE & STORM	03.4	04.3	05.1	06.0	06.8	07.7	08.5	09.4	10.2	11.1	11.9	12.8	13.6	14.5	15.3	16.2	.170
NO. 12	WOOD FRAME EXTERIOR WALLS WITH SHEATHING AND SIDING OR BRICK OR OTHER EXTERIOR FINISH	WINTER TEMP DIFFERENCE
		20	25	30	35	40	45	50	55	60	65	70	75	80	85	90	95	U
	CAVITY INSULATION / SHEATHING
A.	NONE / ½” GYPSUM BOARD (R0.5)	05.4	06.8	08.1	09.5	10.8	12.2	13.6	14.9	16.3	17.6	19.0	20.3	21.7	23.0	24.4	25.7	.271
B.	NONE / ½” ASPHALT BOARD (R1.3)	04.3	05.4	06.5	07.6	08.7	09.8	10.9	11.9	13.0	14.1	15.2	16.3	17.4	18.4	19.5	20.6	.217
C.	R-11 / ½” GYPSUM BOARD (R0.5)	01.8	02.3	02.7	03.2	03.6	04.1	04.5	05.0	05.4	05.9	06.3	06.8	07.2	07.7	08.1	08.6	.090
D.	R-11 / ½” ASPHALT BOARD (R1.3)	01.6	02.0	02.4	02.8	03.2	03.6	04.0	04.4	04.8	05.2	05.6	06.0	06.4	06.8	07.2	07.6	00.1
	R-11 / ½” BEAD BOARD (R1.8)
	R-13 / ½” GYPSUM BOARD (R0.5)
E.	R-11 / ½” EXTR POLY BOARD (R2.5)	01.5	01.9	02.3	02.6	03.0	03.4	03.8	04.1	04.5	04.9	05.3	05.6	06.0	06.4	06.8	07.1	.075
	R-11 / ¾” BEAD BOARD (R2.7)
	R-13 / ½” ASPHALT BOARD (R1.3)
	R-13 / ¾” BEAD BOARD (R1.8)
F.	R-11 / 1” BEAD BOARD (R3.6)	01.4	01.8	02.1	02.5	02.8	03.2	03.5	03.9	04.2	04.6	04.9	05.3	05.6	06.0	06.3	06.7	.070
	R-11 ¾” EXTR POLY BOARD (R3.6)
	R-13 ½” EXTR POLY BOARD (R2.5)
	R-13 ¾” BEAD BOARD (2.7)
G.	R-13 ¾” EXTR POLY BOARD (R3.8)	01.3	01.6	02.0	02.3	02.6	02.9	03.3	03.6	03.9	04.2	04.6	04.9	05.2	05.5	05.9	06.2	.065
	R-13 1” BEAD BOARD (R3.6)
H.	R-11 1” EXTR POLY BOARD (R5.0)	01.2	01.5	01.8	02.1	02.4	02.7	03.0	03.3	03.6	03.9	04.2	04.5	04.8	05.1	05.4	05.7	.060
	R-13 1” EXTR POLY BOARD (R5.0)
	R-19 ¾” GYPSUM BOARD (R0.5)
I.	R-19 ½” ASPHALT BOARD (R1.3)	01.1	01.4	01.7	01.9	02.2	02.5	02.8	03.0	03.3	03.6	03.9	04.1	04.4	04.7	05.0	05.2	.055
	R-19 ½” BEAD BOARD (R1.8)
J.	R-11 R8 SHEATHING	01.0	01.3	01.5	01.8	02.0	02.3	02.5	02.8	03.0	03.3	03.5	03.8	04.0	04.3	04.5	04.8	0.05
	R-13 R8 SHEATHING
	R-19 ½” OR ¾” EXTR POLY BOARD
	R-19 ¾” OR 1” BEAD BOARD
K.	R-19 1” EXTR POLY BOARD (R5.0)	00.9	01.1	01.4	01.6	01.8	02.0	02.3	02.5	02.7	02.9	03.2	03.4	03.6	03.8	04.1	04.3	0.045
L.	R-19 R8 SHEATHING	00.8	01.0	01.2	01.4	01.6	01.8	02.0	02.2	02.4	02.6	02.8	03.0	03.2	03.4	03.6	03.8	0.04
M.	R-27 WALL	00.7	00.9	01.1	01.3	01.5	01.7	01.9	02.0	02.2	02.4	02.6	02.8	03.0	03.1	03.3	03.5	0.037
N.	R-30 WALL	00.7	00.8	01.0	01.2	01.3	01.5	01.7	01.8	02.0	02.1	02.3	02.5	02.6	02.8	03.0	03.1	0.033
O.	R-33 WALL	00.6	00.8	00.9	01.1	01.2	01.4	01.5	01.7	01.8	02.0	02.1	02.3	02.4	02.6	02.7	02.9	0.03
NO. 13	FRAME OR MASONARY PARTITIONS BETWEEN A CONDITIONED AND AN UNCONDITIONED SPACE	USE HTM FROM CONSTRUCTION NO. 12 OR 14. SELECT HTM FOR ACTUAL TEMPERATURE DIFFERENCE EXPECTED ACROSS THE PARTITION

NO. 14	MASONRY WALLS, BLOCK OR BRICK, FINISHED OR UNFINISHED – ABOVE GRADE	WINTER TEMP DIFFERENCE
		20	25	30	35	40	45	50	55	60	65	70	75	80	85	90	95	U
A.	8” OR 12” BLOCK, NO INSUL., UNFIN.	10.2	12.8	15.3	17.9	20.4	23.0	25.5	28.1	30.6	33.2	35.7	38.3	40.8	43.4	45.9	48.5	.510
B.	8” OR 12” BLOCK + R5	02.9	03.6	04.3	05.0	05.8	06.5	07.2	07.9	08.6	09.4	10.1	10.8	11.5	12.2	13.0	13.7	.144
C.	8” OR 12” BLOCK + R11	01.5	01.9	02.3	02.7	03.1	03.5	03.9	04.2	04.6	05.0	05.4	05.8	06.2	06.5	06.9	07.3	.077
D.	8” OR 12” BLOCK + R19	01.0	01.2	01.4	01.7	01.9	02.2	02.4	02.6	02.9	03.1	03.4	03.6	03.8	04.1	04.3	04.6	.048
E.	4” BRICK+ 8” BLOCK, NO INSUL.	08.0	10.0	12.0	14.0	16.0	18.0	20.0	22.0	24.0	26.0	28.0	30.0	32.0	34.0	36.0	38.0	.400
F.	4” BRICK+ 8” BLOCK + R5	02.7	03.3	04.0	04.7	05.3	06.0	06.7	07.3	08.0	08.6	09.3	10.0	10.6	11.3	12.0	12.6	.133
G.	4” BRICK+ 8” BLOCK + R11	01.5	01.9	02.2	02.6	03.0	03.3	03.7	04.1	04.4	04.8	05.2	05.6	05.9	06.3	06.7	07.0	0.074
H.	4” BRICK+ 8” BLOCK + R19	00.9	01.2	01.4	01.6	01.9	02.1	02.4	02.6	02.8	03.1	03.3	03.5	03.8	04.0	04.2	04.5	0.047
NO. 15	MASONRY WALLS, BLOCK OR BRICK, FINISHED OR UNFINISHED – BELOW GRADE	WINTER TEMP DIFFERENCE
		20	25	30	35	40	45	50	55	60	65	70	75	80	85	90	95	U
WALLS EXTEND 2’-5’ BELOW GRADE
A.	8” OR 12” BLOCK + NO INSUL.	02.5	03.1	03.8	04.4	05.0	05.6	06.3	06.9	07.5	08.1	08.8	09.4	10.0	10.6	11.3	11.9	.125
B.	8” OR 12” BLOCK + R5	01.5	01.9	02.2	02.6	03.0	03.3	03.7	04.1	04.4	04.8	05.2	05.6	05.9	06.3	06.7	07.0	.074
C.	8” OR 12” BLOCK + R11	01.0	01.3	01.5	01.8	02.0	02.3	02.6	02.8	03.1	03.3	03.6	03.8	04.1	04.3	04.6	04.8	.051
D.	8” OR 12” BLOCK + R19	00.7	00.9	01.0	01.2	01.4	01.5	01.7	01.9	02.0	02.2	02.4	02.6	02.7	02.9	03.1	03.2	.034
WALLS EXTEND MORE THAN 5’ BELOW GRADE
E.	4” BRICK+ 8” BLOCK, NO INSUL.	01.7	02.2	02.6	03.0	03.5	03.9	04.4	04.8	05.2	05.7	06.1	06.5	07.0	07.4	07.8	08.3	.087
F.	4” BRICK+ 8” BLOCK + R5	01.2	01.5	01.8	02.1	02.4	02.7	03.0	03.2	03.5	03.8	04.1	04.4	04.7	05.0	05.3	05.6	.059
G.	4” BRICK+ 8” BLOCK + R11	00.9	01.1	01.3	01.5	01.7	01.9	02.2	02.4	02.6	02.8	03.0	03.2	03.4	03.7	03.9	04.1	0.043
H.	4” BRICK+ 8” BLOCK + R19	00.6	00.8	00.9	01.1	01.2	01.4	01.6	01.7	01.9	02.0	02.2	02.3	02.5	02.6	02.8	02.9	0.031
NO. 16	CEILINGS UNDER A VENTILATED ATTIC SPACE OR UNHEATED ROOM	WINTER TEMP DIFFERENCE
		20	25	30	35	40	45	50	55	60	65	70	75	80	85	90	95	U
A.	NO INSULATION	12.0	15.0	18.0	21.0	24.0	27.0	30.0	32.9	35.9	38.9	41.9	44.9	47.9	50.9	53.9	56.9	.599
B.	R7 INSULATION	02.4	03.0	03.6	04.2	04.8	05.4	06.0	06.6	07.2	07.8	08.4	09.0	09.6	10.2	10.8	11.4	.120
C.	R11 INSULATION	01.8	02.2	02.6	03.1	03.5	04.0	04.4	04.8	05.3	05.7	06.2	06.6	07.0	07.5	07.9	08.4	.088
D.	R19 INSULATION	01.1	01.3	01.6	01.9	02.1	02.4	02.7	02.9	03.2	03.4	03.7	04.0	04.2	04.5	04.8	05.0	.053
E.	R22 INSULATION	01.0	01.2	01.4	01.7	01.9	02.2	02.4	02.6	02.9	03.1	03.4	03.6	03.8	04.1	04.3	04.6	.048
F.	R26 INSULATION	00.8	01.0	01.1	01.3	01.5	01.7	01.9	02.1	02.3	02.5	02.7	02.9	03.0	03.2	03.4	03.6	.038
G.	R30 INSULATION	00.7	00.8	01.0	01.2	01.3	01.5	01.7	01.8	02.0	02.1	02.3	02.5	02.6	02.8	03.0	03.1	0.033
H.	R38 INSULATION	00.5	00.7	00.8	00.9	01.0	01.2	01.3	01.4	01.6	01.7	01.8	02.0	02.1	02.2	02.3	02.5	0.026
I.	R44 INSULATION	00.5	00.6	00.7	00.8	00.9	01.0	01.2	01.3	01.4	01.5	01.6	01.7	01.8	02.0	02.1	02.2	0.023
J.	R57 INSULATION	00.3	00.4	00.5	00.6	00.7	00.8	00.9	00.9	01.0	01.1	01.2	01.3	01.4	01.4	01.5	01.6	0.017
K.	WOOD DECKING, NO INSULATION	05.7	07.2	08.6	10.0	11.5	12.9	14.4	15.8	17.2	18.7	20.1	21.5	23.0	24.4	25.8	27.3	0.287
NO. 17	ROOF ON EXPOSED BEAMS OR RAFTERS	WINTER TEMP DIFFERENCE
		20	25	30	35	40	45	50	55	60	65	70	75	80	85	90	95	U
A.	1 ½” WOOD DECKING, NO INSUL	06.3	07.9	09.5	11.0	12.6	14.2	15.8	17.3	18.9	20.5	22.1	23.6	25.2	26.8	28.4	29.9	.315
B.	1 ½” WOOD DECKING + R4	02.9	03.6	04.3	05.0	05.8	06.5	07.2	07.9	08.6	09.4	10.1	10.8	11.5	12.2	13.0	13.7	.144
C.	1 ½” WOOD DECKING + R5	02.4	03.1	03.7	04.3	04.9	05.5	06.1	06.7	07.3	07.9	08.5	09.2	09.8	10.4	11.0	11.6	.122
D.	1 ½” WOOD DECKING +R6	02.2	02.7	03.3	03.8	04.4	04.9	05.5	06.0	06.5	07.1	07.6	08.2	08.7	09.3	09.8	10.4	.109
E.	1 ½” WOOD DECKING + R8	01.8	02.2	02.7	03.1	03.6	04.0	04.5	04.9	05.3	05.8	06.2	06.7	07.1	07.6	08.0	08.5	.089
F.	2” SHREDDED WOOD PLANKS	04.3	05.4	06.5	07.6	08.7	09.8	10.9	11.9	13.0	14.1	15.2	16.3	17.4	18.4	19.5	20.6	.217
G.	3” SHREDDED WOOD PLANKS	03.2	04.0	04.8	05.6	06.4	07.2	08.0	08.7	09.5	10.3	11.1	11.9	12.7	13.5	14.3	15.1	0.159
H.	1 ½” FIBER BOARD INSULATION	03.5	04.4	05.3	06.1	07.0	07.9	08.8	09.6	10.5	11.4	12.3	13.1	14.0	14.9	15.8	16.6	0.175
I.	2” FIBER BOARD INSULATION	02.8	03.5	04.2	04.9	05.6	06.3	07.0	07.7	08.4	09.1	09.8	10.5	11.2	11.9	12.6	13.3	0.14
J.	3”FIBER BOARD INSULATION	02.0	02.5	03.0	03.5	04.0	04.5	05.0	05.4	05.9	06.4	06.9	07.4	07.9	08.4	08.9	09.4	0.099
K.	1 ½” WOOD DECKING + R13	01.2	01.5	01.8	02.1	02.4	02.7	03.0	03.3	03.6	03.9	04.2	04.5	04.8	05.1	05.4	05.7	0.06
L.	1 ½” WOOD DECKING + R19	00.8	01.0	01.2	01.4	01.6	01.8	02.1	02.3	02.5	02.7	02.9	03.1	03.3	03.5	03.7	03.9	0.041
NO. 18	ROOF-CEILING COMBINATION	WINTER TEMP DIFFERENCE
		20	25	30	35	40	45	50	55	60	65	70	75	80	85	90	95	U
A.	NO INSULATION	06.2	07.7	09.2	10.8	12.3	13.9	15.4	16.9	18.5	20.0	21.6	23.1	24.6	26.2	27.7	29.3	.308
B.	R11 BATTS	01.4	01.8	02.2	02.5	02.9	03.2	03.6	04.0	04.3	04.7	05.0	05.4	05.8	06.1	06.5	06.8	.072
C.	R19 BATTS (2” X 8” RAFTERS)	01.0	01.2	01.5	01.7	02.0	02.2	02.5	02.7	02.9	03.2	03.4	03.7	03.9	04.2	04.4	04.7	.049
D.	R22 BATTS (2” X 8” RAFTERS)	00.9	01.1	01.4	01.6	01.8	02.0	02.3	02.5	02.7	02.9	03.2	03.4	03.6	03.8	04.1	04.3	.045
E.	R26 BATTS (2” X 8” RAFTERS)	00.8	01.0	01.2	01.4	01.6	01.8	02.0	02.2	02.4	02.6	02.8	03.0	03.2	03.4	03.6	03.8	.040
F.	R30 BATTS (2” X 10” RAFTERS)	00.7	00.9	01.1	01.2	01.4	01.6	01.8	01.9	02.1	02.3	02.5	02.6	02.8	03.0	03.2	03.3	.035
NO. 19	FLOORS OVER AN UNHEATED BASEMENT, ENCLOSED CRAWLSPACE, OR CRAWLSPACE WITH CLOSABLE VENTS	WINTER TEMP DIFFERENCE
		20	25	30	35	40	45	50	55	60	65	70	75	80	85	90	95	U
A.	HARDWOOD FLOOR + NO INSULATION	03.1	03.9	04.7	05.5	06.2	07.0	07.8	08.6	09.4	10.1	10.9	11.7	12.5	13.3	14.0	14.8	.156
B.	HARDWOOD FLOOR + R11	00.8	01.0	01.2	01.4	01.6	01.8	02.0	02.2	02.4	02.6	02.8	03.0	03.2	03.4	03.6	03.8	.040
C.	HARDWOOD FLOOR + R13	00.8	01.0	01.1	01.3	01.5	01.7	01.9	02.1	02.3	02.5	02.7	02.9	03.0	03.2	03.4	03.6	.038
D.	HARDWOOD FLOOR + R19	00.5	00.7	00.8	00.9	01.0	01.2	01.3	01.4	01.6	01.7	01.8	02.0	02.1	02.2	02.3	02.5	.026
E.	HARDWOOD FLOOR + R30	00.4	00.5	00.5	00.6	00.7	00.8	00.9	01.0	01.1	01.2	01.3	01.4	01.4	01.5	01.6	01.7	.018
F.	CARPETED FLOOR + NO INSULATION	02.2	02.7	03.3	03.8	04.4	04.9	05.5	06.0	06.5	07.1	07.6	08.2	08.7	09.3	09.8	10.4	.109
G.	CARPETED FLOOR + R11	00.7	00.9	01.1	01.2	01.4	01.6	01.8	01.9	02.1	02.3	02.5	02.6	02.8	03.0	03.2	03.3	0.035
H.	CARPETED FLOOR + R13	00.7	00.9	01.0	01.2	01.4	01.5	01.7	01.9	02.0	02.2	02.4	02.6	02.7	02.9	03.1	03.2	0.034
I.	CARPETED FLOOR + R19	00.5	00.6	00.7	00.8	01.0	01.1	01.2	01.3	01.4	01.6	01.7	01.8	01.9	02.0	02.2	02.3	0.024
J.	CARPETED FLOOR + R30	00.4	00.4	00.5	00.6	00.7	00.8	00.9	01.0	01.1	01.1	01.2	01.3	01.4	01.5	01.6	01.7	0.0175
NO. 20	FLOORS OVER AN OPEN CRAWLSPACE OR GARAGE	WINTER TEMP DIFFERENCE
		20	25	30	35	40	45	50	55	60	65	70	75	80	85	90	95	U
A.	HARDWOOD FLOOR + NO INSULATION	06.2	07.8	09.4	10.9	12.5	14.0	15.6	17.2	18.7	20.3	21.8	23.4	25.0	26.5	28.1	29.6	.312
B.	HARDWOOD FLOOR + R11	01.6	02.0	02.4	02.8	03.2	03.6	04.0	04.4	04.8	05.2	05.6	06.0	06.4	06.8	07.2	07.6	.080
C.	HARDWOOD FLOOR + R13	01.5	01.9	02.3	02.7	03.0	03.4	03.8	04.2	04.6	04.9	05.3	05.7	06.1	06.5	06.8	07.2	.076
D.	HARDWOOD FLOOR + R19	01.0	01.3	01.6	01.8	02.1	02.3	02.6	02.9	03.1	03.4	03.6	03.9	04.2	04.4	04.7	04.9	.052
E.	HARDWOOD FLOOR + R30	00.7	00.9	01.1	01.3	01.5	01.7	01.9	02.0	02.2	02.4	02.6	02.8	03.0	03.1	03.3	03.5	.037
F.	CARPETED FLOOR + NO INSULATION	04.4	05.5	06.5	07.6	08.7	09.8	10.9	12.0	13.1	14.2	15.3	16.4	17.4	18.5	19.6	20.7	.218
G.	CARPETED FLOOR + R11	01.4	01.8	02.1	02.5	02.8	03.2	03.6	03.9	04.3	04.6	05.0	05.3	05.7	06.0	06.4	06.7	0.071
H.	CARPETED FLOOR + R13	01.4	01.7	02.0	02.4	02.7	03.1	03.4	03.7	04.1	04.4	04.8	05.1	05.4	05.8	06.1	06.5	0.068
I.	CARPETED FLOOR + R19	01.0	01.2	01.4	01.7	01.9	02.2	02.4	02.6	02.9	03.1	03.4	03.6	03.8	04.1	04.3	04.6	0.048
J.	CARPETED FLOOR + R30	00.7	00.9	01.1	01.2	01.4	01.6	01.8	01.9	02.1	02.3	02.5	02.6	02.8	03.0	03.2	03.3	0.035
NO. 21	BASEMENT FLOORS	WINTER TEMP DIFFERENCE
		20	25	30	35	40	45	50	55	60	65	70	75	80	85	90	95	U

A.	2 OR MORE FEET BELOW GRADE	00.5	00.6	00.7	00.8	01.0	01.1	01.2	01.3	01.4	01.6	01.7	01.8	01.9	02.0	02.2	02.3	.024
NO. 22	CONCRETE SLAB ON GRADE	WINTER TEMP DIFFERENCE
		20	25	30	35	40	45	50	55	60	65	70	75	80	85	90	95	U
A.	NO EDGE INSULATION	16.2	20.3	24.3	28.4	32.4	36.5	40.5	44.6	48.6	52.7	56.7	60.8	64.8	68.9	72.9	77.0	.810
B.	1” EDGE INSULATION (R5)	08.2	10.3	12.3	14.4	16.4	18.5	20.5	22.6	24.6	26.7	28.7	30.8	32.8	34.9	36.9	39.0	.410
C.	1 ½” EDGE INSULATION (R8)	05.4	06.8	08.1	09.5	10.8	12.2	13.5	14.9	16.2	17.6	18.9	20.3	21.6	23.0	24.3	25.7	.270
D.	2” EDGE INSULATION (R11)	04.2	05.3	06.3	07.4	08.4	09.5	10.5	11.6	12.6	13.7	14.7	15.8	16.8	17.9	18.9	20.0	.210
NO. 23	CONCRETE SLAB WITH PERIMETER WARM AIR DUCT SYSTEM	WINTER TEMP DIFFERENCE
		20	25	30	35	40	45	50	55	60	65	70	75	80	85	90	95	U
A.	NO EDGE INSULATION	38.0	47.5	57.0	66.5	76.0	85.5	95.0	104.5	114.0	123.5	133.0	142.5	152.0	161.5	171.0	180.5	1.900
B.	1” EDGE INSULATION (R5)	22.8	28.5	34.2	39.9	45.6	51.3	57.0	62.7	68.4	74.1	79.8	85.5	91.2	96.9	102.6	108.3	1.140
C.	1 ½” EDGE INSULATION (R8)	20.0	25.0	30.0	35.0	40.0	45.0	50.0	55.0	60.0	65.0	70.0	75.0	80.0	85.0	90.0	95.0	1.000
D.	2” EDGE INSULATION (R11)	18.6	23.3	27.9	32.6	37.2	41.9	46.5	51.2	55.8	60.5	65.1	69.8	74.4	79.1	83.7	88.4	.930

## TABLE 3A
TABLE 3A
GLASS HEAT TRANSFER MULTIPLIERS (COOLING)
NO EXTERNAL SHADE SCREEN
CLEAR GLASS
	SINGLE PANE					DOUBLE PANE AND SINGLE PANE LOW E COATING					TRIPLE PANE AND DOUBLE PANE LOW E COATING
DESIGN TEMP DIFFERENCE	10	15	20	25	30	35		10	15	20	25	30	35		10	15	20	25	30	35
DIRECTION WINDOW FACES	NO INTERNAL SHADING	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!			2	4	6	8	10			1	2	3	4	5
N	23	27	31	35	39	43		19	21	23	25	27	29		17	18	19	20	21	22
NE AND NW	56	60	64	68	72	76		47	48	49	50	51	52		43	44	45	46	47	48
E AND W	81	85	89	93	97	101		68	70	72	74	76	78		62	63	64	65	66	67
SE AND SW	70	74	78	82	86	90		59	61	63	65	67	69		53	54	55	56	57	58
S	40	44	48	52	56	60		34	36	38	40	42	44		30	31	32	33	34	35
	DRAPERIES OR VENETIAN BLINDS
N	14	18	22	26	30	34		12	14	16	18	20	22		10	11	12	13	14	15
NE AND NW	33	37	41	45	49	53		29	31	33	35	37	39		25	26	27	28	29	30
E AND W	48	52	56	60	64	68		42	44	46	48	50	52		37	38	39	40	41	42
SE AND SW	41	45	49	53	57	61		37	39	41	43	45	47		32	33	34	35	36	37
S	24	28	32	36	40	44		21	23	25	27	29	31		18	19	20	21	22	23
	ROLLER SHADES – HALF DRAWN
N	17	21	25	29	33	37		16	18	20	22	24	26		14	15	16	17	18	19
NE AND NW	41	45	49	53	57	61		38	40	42	44	46	48		34	35	36	37	38	39
E AND W	60	64	68	72	76	80		55	57	59	61	63	65		49	50	51	52	53	54
SE AND SW	52	56	60	64	68	72		47	49	51	53	55	57		42	43	44	45	46	47
S	30	34	38	42	46	50		27	29	31	33	35	37		24	25	26	27	28	29
	AWNING, PORCHES, OR OTHER EXTERNAL SHADING
ALL DIRECTIONS	23	27	31	35	39	43		19	21	23	25	27	29		17	18	19	20	21	22
TINTED (HEAT ABSORBING) GLASS
	SINGLE PANE					DOUBLE PANE AND SINGLE PANE LOW E COATING					TRIPLE PANE AND DOUBLE PANE LOW E COATING
DESIGN TEMP DIFFERENCE	10	15	20	25	30	35		10	15	20	25	30	35		10	15	20	25	30	35
DIRECTION WINDOW FACES	NO INTERNAL SHADING	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!			2	4	6	8	10			1	2	3	4	5
N	16	20	24	28	32	36		12	14	16	18	20	22		9	10	11	12	13	14
NE AND NW	39	43	47	51	55	59		29	31	33	35	37	39		22	23	24	25	26	27
E AND W	57	61	65	69	73	77		42	44	46	48	50	52		32	33	34	35	36	37
SE AND SW	49	53	57	61	65	69		36	38	40	42	44	46		28	29	30	31	32	33
S	28	32	36	40	44	48		21	23	25	27	29	31		16	17	18	19	20	21
	DRAPERIES OR VENETIAN BLINDS
N	12	16	20	24	28	32		9	11	13	15	17	19		6	7	8	9	10	11
NE AND NW	30	34	38	42	46	50		22	24	26	28	30	32		15	16	17	18	19	20
E AND W	43	47	51	55	59	63		31	33	35	37	39	41		21	22	23	24	25	26
SE AND SW	37	41	45	49	53	57		27	29	31	33	35	37		18	19	20	21	22	23
S	21	25	29	33	37	41		15	17	19	21	23	25		10	11	12	13	14	15
	ROLLER SHADES – HALF DRAWN
N	14	18	22	26	30	34		10	12	14	16	18	20		7	8	9	10	11	12
NE AND NW	34	38	42	46	50	54		25	27	29	31	33	35		18	19	20	21	22	23
E AND W	49	53	57	61	65	69		36	38	40	42	44	46		26	27	28	29	30	31
SE AND SW	42	46	50	54	58	62		31	33	35	37	39	41		22	23	24	25	26	27
S	24	28	32	36	40	44		18	20	22	24	26	28		13	14	15	16	17	18
	AWNING, PORCHES, OR OTHER EXTERNAL SHADING
ALL DIRECTIONS	16	20	24	28	32	36		12	14	16	18	20	22		9	10	11	12	13	14
REFLECTIVE COATED GLASS
	SINGLE PANE					DOUBLE PANE AND SINGLE PANE LOW E COATING					TRIPLE PANE AND DOUBLE PANE LOW E COATING
DESIGN TEMP DIFFERENCE	10	15	20	25	30	35		10	15	20	25	30	35		10	15	20	25	30	35
DIRECTION WINDOW FACES	NO INTERNAL SHADING	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!			2	4	6	8	10			1	2	3	4	5
N	14	18	22	26	30	34		10	12	14	16	18	20		6	7	8	9	10	11
NE AND NW	34	38	42	46	50	54		24	26	28	30	32	34		15	16	17	18	19	20
E AND W	49	53	57	61	65	69		34	36	38	40	42	44		21	22	23	24	25	26
SE AND SW	43	47	51	55	59	63		29	31	33	35	37	39		18	19	20	21	22	23
S	24	28	32	36	40	44		17	19	21	23	25	27		10	11	12	13	14	15
	DRAPERIES OR VENETIAN BLINDS
N	11	15	19	23	27	31		8	10	12	14	16	18		5	6	7	8	9	10
NE AND NW	28	32	36	40	44	48		20	22	24	26	28	30		12	13	14	15	16	17
E AND W	40	44	48	52	56	60		30	32	34	36	38	40		17	18	19	20	21	22
SE AND SW	35	39	43	47	51	55		26	28	30	32	34	36		15	16	17	18	19	20
S	20	24	28	32	36	40		15	17	19	21	23	25		9	10	11	12	13	14
	ROLLER SHADES – HALF DRAWN
N	12	16	20	24	28	32		9	11	13	15	17	19		5	6	7	8	9	10
NE AND NW	30	34	38	42	46	50		21	23	25	27	29	31		13	14	15	16	17	18
E AND W	44	48	52	56	60	64		31	33	35	37	39	41		18	19	20	21	22	23
SE AND SW	38	42	46	50	54	58		27	29	31	33	35	37		16	17	18	19	20	21
S	22	26	30	34	38	42		15	17	19	21	23	25		9	10	11	12	13	14
	AWNING, PORCHES, OR OTHER EXTERNAL SHADING
ALL DIRECTIONS	14	18	22	26	30	34		10	12	14	16	18	20		6	7	8	9	10	11

## TABLE 3B
TABLE 3B
GLASS HEAT TRANSFER MULTIPLIERS (COOLING)
EXTERNAL SHADE SCREEN, SHADING COEFFICIENT = .15
CLEAR GLASS
	SINGLE PANE					DOUBLE PANE AND SINGLE PANE LOW E COATING					TRIPLE PANE AND DOUBLE PANE LOW E COATING
DESIGN TEMP DIFFERENCE	10	15	20	25	30	35		10	15	20	25	30	35		10	15	20	25	30	35
DIRECTION WINDOW FACES	NO INTERNAL SHADING	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!			2	4	6	8	10			1	2	3	4	5
N	23	27	31	35	39	43		19	21	23	25	27	29		17	18	19	20	21	22
NE AND NW	28	32	36	40	44	48		23	25	27	29	31	33		21	22	23	24	25	26
E AND W	32	36	40	44	48	52		26	28	30	32	34	36		24	25	26	27	28	29
SE AND SW	30	34	38	42	46	50		25	27	29	31	33	35		22	23	24	25	26	27
S	26	30	34	38	42	46		21	23	25	27	29	31		19	20	21	22	23	24
	DRAPERIES OR VENETIAN BLINDS	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!			2	4	6	8	10			1	2	3	4	5
N	14	18	22	26	30	34		12	14	16	18	20	22		10	11	12	13	14	15
NE AND NW	17	21	25	29	33	37		15	17	19	21	23	25		12	13	14	15	16	17
E AND W	19	23	27	31	35	39		17	19	21	23	25	27		14	15	16	17	18	19
SE AND SW	18	22	26	30	34	38		16	18	20	22	24	26		13	14	15	16	17	18
S	16	20	24	28	32	36		13	15	17	19	21	23		11	12	13	14	15	16
	ROLLER SHADES – HALF DRAWN	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!			2	4	6	8	10			1	2	3	4	5
N	17	21	25	29	33	37		16	18	20	22	24	26		14	15	16	17	18	19
NE AND NW	21	25	29	33	37	41		19	21	23	25	27	29		17	18	19	20	21	22
E AND W	23	27	31	35	39	43		22	24	26	28	30	32		19	20	21	22	23	24
SE AND SW	22	26	30	34	38	42		21	23	25	27	29	31		18	19	20	21	22	23
S	19	23	27	31	35	39		18	20	22	24	26	28		16	17	18	19	20	21
TINTED (HEAT ABSORBING) GLASS
	SINGLE PANE					DOUBLE PANE AND SINGLE PANE LOW E COATING					TRIPLE PANE AND DOUBLE PANE LOW E COATING
DESIGN TEMP DIFFERENCE	10	15	20	25	30	35		10	15	20	25	30	35		10	15	20	25	30	35
DIRECTION WINDOW FACES	NO INTERNAL SHADING	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!			2	4	6	8	10			1	2	3	4	5
N	16	20	24	28	32	36		12	14	16	18	20	22		9	10	11	12	13	14
NE AND NW	19	23	27	31	35	39		15	17	19	21	23	25		11	12	13	14	15	16
E AND W	22	26	30	34	38	42		17	19	21	23	25	27		12	13	14	15	16	17
SE AND SW	21	25	29	33	37	41		16	18	20	22	24	26		12	13	14	15	16	17
S	18	22	26	30	34	38		13	15	17	19	21	23		10	11	12	13	14	15
	DRAPERIES OR VENETIAN BLINDS	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!			2	4	6	8	10
N	12	16	20	24	28	32		9	11	13	15	17	19		6	7	8	9	10	11
NE AND NW	15	19	23	27	31	35		11	13	15	17	19	21		7	8	9	10	11	12
E AND W	17	21	25	29	33	37		12	14	16	18	20	22		8	9	10	11	12	13
SE AND SW	16	20	24	28	32	36		12	14	16	18	20	22		8	9	10	11	12	13
S	13	17	21	25	29	33		10	12	14	16	18	20		7	8	9	10	11	12
	ROLLER SHADES – HALF DRAWN	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!			2	4	6	8	10
N	14	18	22	26	30	34		10	12	14	16	18	20		7	8	9	10	11	12
NE AND NW	17	21	25	29	33	37		12	14	16	18	20	22		9	10	11	12	13	14
E AND W	19	23	27	31	35	39		14	16	18	20	22	24		10	11	12	13	14	15
SE AND SW	18	22	26	30	34	38		13	15	17	19	21	23		9	10	11	12	13	14
S	16	20	24	28	32	36		11	13	15	17	19	21		8	9	10	11	12	13
REFLECTIVE COATED GLASS
	SINGLE PANE					DOUBLE PANE AND SINGLE PANE LOW E COATING					TRIPLE PANE AND DOUBLE PANE LOW E COATING
DESIGN TEMP DIFFERENCE	10	15	20	25	30	35		10	15	20	25	30	35		10	15	20	25	30	35
DIRECTION WINDOW FACES	NO INTERNAL SHADING	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!			2	4	6	8	10			1	2	3	4	5
N	14	18	22	26	30	34		10	12	14	16	18	20		6	7	8	9	10	11
NE AND NW	17	21	25	29	33	37		12	14	16	18	20	22		7	8	9	10	11	12
E AND W	19	23	27	31	35	39		14	16	18	20	22	24		8	9	10	11	12	13
SE AND SW	18	22	26	30	34	38		13	15	17	19	21	23		8	9	10	11	12	13
S	16	20	24	28	32	36		11	13	15	17	19	21		7	8	9	10	11	12
	DRAPERIES OR VENETIAN BLINDS	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!			2	4	6	8	10
N	11	15	19	23	27	31		8	10	12	14	16	18		5	6	7	8	9	10
NE AND NW	14	18	22	26	30	34		10	12	14	16	18	20		6	7	8	9	10	11
E AND W	15	19	23	27	31	35		11	13	15	17	19	21		7	8	9	10	11	12
SE AND SW	15	19	23	27	31	35		11	13	15	17	19	21		7	8	9	10	11	12
S	12	16	20	24	28	32		9	11	13	15	17	19		6	7	8	9	10	11
	ROLLER SHADES – HALF DRAWN	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!			2	4	6	8	10
N	12	16	20	24	28	32		9	11	13	15	17	19		5	6	7	8	9	10
NE AND NW	15	19	23	27	31	35		11	13	15	17	19	21		6	7	8	9	10	11
E AND W	17	21	25	29	33	37		12	14	16	18	20	22		7	8	9	10	11	12
SE AND SW	16	20	24	28	32	36		12	14	16	18	20	22		7	8	9	10	11	12
S	14	18	22	26	30	34		10	12	14	16	18	20		6	7	8	9	10	11

## TABLE 3C
TABLE 3C
GLASS HEAT TRANSFER MULTIPLIERS (COOLING)
EXTERNAL SHADE SCREEN, SHADING COEFFICIENT = .25
CLEAR GLASS
	SINGLE PANE					DOUBLE PANE AND SINGLE PANE LOW E COATING					TRIPLE PANE AND DOUBLE PANE LOW E COATING
DESIGN TEMP DIFFERENCE	10	15	20	25	30	35		10	15	20	25	30	35		10	15	20	25	30	35
DIRECTION WINDOW FACES	NO INTERNAL SHADING	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!			2	4	6	8	10			1	2	3	4	5
N	23	27	31	35	39	43		19	21	23	25	27	29		17	18	19	20	21	22
NE AND NW	31	35	39	43	47	51		26	28	30	32	34	36		24	25	26	27	28	29
E AND W	38	42	46	50	54	58		31	33	35	37	39	41		28	29	30	31	32	33
SE AND SW	35	39	43	47	51	55		29	31	33	35	37	39		26	27	28	29	30	31
S	27	31	35	39	43	47		23	25	27	29	31	33		20	21	22	23	24	25
	DRAPERIES OR VENETIAN BLINDS	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!			2	4	6	8	10			1	2	3	4	5
N	14	18	22	26	30	34		12	14	16	18	20	22		10	11	12	13	14	15
NE AND NW	19	23	27	31	35	39		16	18	20	22	24	26		14	15	16	17	18	19
E AND W	23	27	31	35	39	43		20	22	24	26	28	30		17	18	19	20	21	22
SE AND SW	21	25	29	33	37	41		18	20	22	24	26	28		16	17	18	19	20	21
S	17	21	25	29	33	37		14	16	18	20	22	24		12	13	14	15	16	17
	ROLLER SHADES – HALF DRAWN	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!			2	4	6	8	10			1	2	3	4	5
N	17	21	25	29	33	37		16	18	20	22	24	26		14	15	16	17	18	19
NE AND NW	23	27	31	35	39	43		22	24	26	28	30	32		19	20	21	22	23	24
E AND W	28	32	36	40	44	48		26	28	30	32	34	36		23	24	25	26	27	28
SE AND SW	26	30	34	38	42	46		24	26	28	30	32	34		21	22	23	24	25	26
S	20	24	28	32	36	40		19	21	23	25	27	29		17	18	19	20	21	22
TINTED (HEAT ABSORBING) GLASS
	SINGLE PANE					DOUBLE PANE AND SINGLE PANE LOW E COATING					TRIPLE PANE AND DOUBLE PANE LOW E COATING
DESIGN TEMP DIFFERENCE	10	15	20	25	30	35		10	15	20	25	30	35		10	15	20	25	30	35
DIRECTION WINDOW FACES	NO INTERNAL SHADING	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!			2	4	6	8	10			1	2	3	4	5
N	16	20	24	28	32	36		12	14	16	18	20	22		9	10	11	12	13	14
NE AND NW	22	26	30	34	38	42		14	16	18	20	22	24		12	13	14	15	16	17
E AND W	26	30	34	38	42	46		20	22	24	26	28	30		15	16	17	18	19	20
SE AND SW	24	28	32	36	40	44		18	20	22	24	26	28		14	15	16	17	18	19
S	19	23	27	31	35	39		14	16	18	20	22	24		11	12	13	14	15	16
	DRAPERIES OR VENETIAN BLINDS	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!			2	4	6	8	10			1	2	3	4	5
N	12	16	20	24	28	32		9	11	13	15	17	19		6	7	8	9	10	11
NE AND NW	17	21	25	29	33	37		12	14	16	18	20	22		8	9	10	11	12	13
E AND W	20	24	28	32	36	40		15	17	19	21	23	25		10	11	12	13	14	15
SE AND SW	18	22	26	30	34	38		14	16	18	20	22	24		9	10	11	12	13	14
S	14	18	22	26	30	34		11	13	15	17	19	21		7	8	9	10	11	12
	ROLLER SHADES – HALF DRAWN	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!			2	4	6	8	10			1	2	3	4	5
N	14	18	22	26	30	34		10	12	14	16	18	20		7	8	9	10	11	12
NE AND NW	19	23	27	31	35	39		14	16	18	20	22	24		10	11	12	13	14	15
E AND W	23	27	31	35	39	43		17	19	21	23	25	27		12	13	14	15	16	17
SE AND SW	21	25	29	33	37	41		15	17	19	21	23	25		11	12	13	14	15	16
S	17	21	25	29	33	37		12	14	16	18	20	22		9	10	11	12	13	14
REFLECTIVE COATED GLASS
	SINGLE PANE					DOUBLE PANE AND SINGLE PANE LOW E COATING					TRIPLE PANE AND DOUBLE PANE LOW E COATING
DESIGN TEMP DIFFERENCE	10	15	20	25	30	35		10	15	20	25	30	35		10	15	20	25	30	35
DIRECTION WINDOW FACES	NO INTERNAL SHADING	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!			2	4	6	8	10			1	2	3	4	5
N	14	18	22	26	30	34		10	12	14	16	18	20		6	7	8	9	10	11
NE AND NW	19	23	27	31	35	39		14	16	18	20	22	24		8	9	10	11	12	13
E AND W	23	27	31	35	39	43		16	18	20	22	24	26		10	11	12	13	14	15
SE AND SW	21	25	29	33	37	41		15	17	19	21	23	25		9	10	11	12	13	14
S	17	21	25	29	33	37		12	14	16	18	20	22		7	8	9	10	11	12
	DRAPERIES OR VENETIAN BLINDS	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!			2	4	6	8	10			1	2	3	4	5
N	11	15	19	23	27	31		8	10	12	14	16	18		5	6	7	8	9	10
NE AND NW	15	19	23	27	31	35		11	13	15	17	19	21		7	8	9	10	11	12
E AND W	18	22	26	30	34	38		14	16	18	20	22	24		8	9	10	11	12	13
SE AND SW	17	21	25	29	33	37		13	15	17	19	21	23		8	9	10	11	12	13
S	13	17	21	25	29	33		10	12	14	16	18	20		6	7	8	9	10	11
	ROLLER SHADES – HALF DRAWN	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!			2	4	6	8	10			1	2	3	4	5
N	12	16	20	24	28	32		9	11	13	15	17	19		5	6	7	8	9	10
NE AND NW	17	21	25	29	33	37		12	14	16	18	20	22		7	8	9	10	11	12
E AND W	20	24	28	32	36	40		15	17	19	21	23	25		8	9	10	11	12	13
SE AND SW	19	23	27	31	35	39		14	16	18	20	22	24		8	9	10	11	12	13
S	15	19	23	27	31	35		11	13	15	17	19	21		6	7	8	9	10	11

## TABLE 3D
TABLE 3D
GLASS HEAT TRANSFER MULTIPLIERS (COOLING)
EXTERNAL SHADE SCREEN, SHADING COEFFICIENT = .35
CLEAR GLASS
	SINGLE PANE					DOUBLE PANE AND SINGLE PANE LOW E COATING					TRIPLE PANE AND DOUBLE PANE LOW E COATING
DESIGN TEMP DIFFERENCE	10	15	20	25	30	35		10	15	20	25	30	35		10	15	20	25	30	35
DIRECTION WINDOW FACES	NO INTERNAL SHADING	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!			2	4	6	8	10			1	2	3	4	5
N	23	27	31	35	39	43		19	21	23	25	27	29		17	18	19	20	21	22
NE AND NW	35	39	43	47	51	55		29	31	33	35	37	39		26	27	28	29	30	31
E AND W	43	47	51	55	59	63		36	38	40	42	44	46		33	34	35	36	37	38
SE AND SW	39	43	47	51	55	59		33	35	37	39	41	43		30	31	32	33	34	35
S	29	33	37	41	45	49		24	26	28	30	32	34		22	23	24	25	26	27
	DRAPERIES OR VENETIAN BLINDS	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!			2	4	6	8	10			1	2	3	4	5
N	14	18	22	26	30	34		12	14	16	18	20	22		10	11	12	13	14	15
NE AND NW	21	25	29	33	37	41		18	20	22	24	26	28		15	16	17	18	19	20
E AND W	26	30	34	38	42	46		23	25	27	29	31	33		19	20	21	22	23	24
SE AND SW	23	27	31	35	39	43		21	23	25	27	29	31		18	19	20	21	22	23
S	18	22	26	30	34	38		15	17	19	21	23	25		13	14	15	16	17	18
	ROLLER SHADES – HALF DRAWN	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!			2	4	6	8	10			1	2	3	4	5
N	17	21	25	29	33	37		16	18	20	22	24	26		14	15	16	17	18	19
NE AND NW	25	29	33	37	41	45		24	26	28	30	32	34		21	22	23	24	25	26
E AND W	32	36	40	44	48	52		30	32	34	36	38	40		26	27	28	29	30	31
SE AND SW	29	33	37	41	45	49		27	29	31	33	35	37		24	25	26	27	28	29
S	22	26	30	34	38	42		20	22	24	26	28	30		18	19	20	21	22	23
TINTED (HEAT ABSORBING) GLASS		4	8	12	16	20			2	4	6	8	10			1	2	3	4	5
	SINGLE PANE	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!		DOUBLE PANE AND SINGLE PANE LOW E COATING	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!		TRIPLE PANE AND DOUBLE PANE LOW E COATING	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!
DESIGN TEMP DIFFERENCE	10	14	18	22	26	30		10	12	14	16	18	20		10	11	12	13	14	15
DIRECTION WINDOW FACES	NO INTERNAL SHADING	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!			2	4	6	8	10			1	2	3	4	5
N	16	20	24	28	32	36		12	14	16	18	20	22		9	10	11	12	13	14
NE AND NW	24	28	32	36	40	44		18	20	22	24	26	28		14	15	16	17	18	19
E AND W	30	34	38	42	46	50		23	25	27	29	31	33		17	18	19	20	21	22
SE AND SW	28	32	36	40	44	48		20	22	24	26	28	30		16	17	18	19	20	21
S	20	24	28	32	36	40		15	17	19	21	23	25		11	12	13	14	15	16
	DRAPERIES OR VENETIAN BLINDS	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!			2	4	6	8	10			1	2	3	4	5
N	12	16	20	24	28	32		9	11	13	15	17	19		6	7	8	9	10	11
NE AND NW	18	22	26	30	34	38		14	16	18	20	22	24		9	10	11	12	13	14
E AND W	23	27	31	35	39	43		17	19	21	23	25	27		11	12	13	14	15	16
SE AND SW	21	25	29	33	37	41		15	17	19	21	23	25		10	11	12	13	14	15
S	15	19	23	27	31	35		11	13	15	17	19	21		7	8	9	10	11	12
	ROLLER SHADES – HALF DRAWN	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!			2	4	6	8	10			1	2	3	4	5
N	14	18	22	26	30	34		10	12	14	16	18	20		7	8	9	10	11	12
NE AND NW	21	25	29	33	37	41		15	17	19	21	23	25		11	12	13	14	15	16
E AND W	26	30	34	38	42	46		19	21	23	25	27	29		14	15	16	17	18	19
SE AND SW	24	28	32	36	40	44		17	19	21	23	25	27		12	13	14	15	16	17
S	18	22	26	30	34	38		13	15	17	19	21	23		9	10	11	12	13	14
REFLECTIVE COATED GLASS		4	8	12	16	20			2	4	6	8	10			1	2	3	4	5
	SINGLE PANE	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!		DOUBLE PANE AND SINGLE PANE LOW E COATING	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!		TRIPLE PANE AND DOUBLE PANE LOW E COATING	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!
DESIGN TEMP DIFFERENCE	10	14	18	22	26	30		10	12	14	16	18	20		10	11	12	13	14	15
DIRECTION WINDOW FACES	NO INTERNAL SHADING	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!			2	4	6	8	10			1	2	3	4	5
N	14	18	22	26	30	34		10	12	14	16	18	20		6	7	8	9	10	11
NE AND NW	21	25	29	33	37	41		15	17	19	21	23	25		9	10	11	12	13	14
E AND W	26	30	34	38	42	46		18	20	22	24	26	28		11	12	13	14	15	16
SE AND SW	24	28	32	36	40	44		17	19	21	23	25	27		10	11	12	13	14	15
S	18	22	26	30	34	38		12	14	16	18	20	22		7	8	9	10	11	12
	DRAPERIES OR VENETIAN BLINDS	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!			2	4	6	8	10			1	2	3	4	5
N	11	15	19	23	27	31		8	10	12	14	16	18		5	6	7	8	9	10
NE AND NW	17	21	25	29	33	37		12	14	16	18	20	22		7	8	9	10	11	12
E AND W	21	25	29	33	37	41		16	18	20	22	24	26		9	10	11	12	13	14
SE AND SW	19	23	27	31	35	39		14	16	18	20	22	24		9	10	11	12	13	14
S	14	18	22	26	30	34		10	12	14	16	18	20		6	7	8	9	10	11
	ROLLER SHADES – HALF DRAWN	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!			2	4	6	8	10			1	2	3	4	5
N	12	16	20	24	28	32		9	11	13	15	17	19		5	6	7	8	9	10
NE AND NW	18	22	26	30	34	38		13	15	17	19	21	23		8	9	10	11	12	13
E AND W	23	27	31	35	39	43		17	19	21	23	25	27		10	11	12	13	14	15
SE AND SW	21	25	29	33	37	41		15	17	19	21	23	25		9	10	11	12	13	14
S	16	20	24	28	32	36		11	13	15	17	19	21		6	7	8	9	10	11

## TABLE 3E
TABLE 3E
GLASS HEAT TRANSFER MULTIPLIERS (COOLING)
EXTERNAL SHADE SCREEN, SHADING COEFFICIENT = .45 OR ADJUSTABLE BLINDS BETWEEN GLAZING (DOUBLE PANE ONLY)
CLEAR GLASS
	SINGLE PANE					DOUBLE PANE AND SINGLE PANE LOW E COATING					TRIPLE PANE AND DOUBLE PANE LOW E COATING
DESIGN TEMP DIFFERENCE	10	15	20	25	30	35		10	15	20	25	30	35		10	15	20	25	30	35
DIRECTION WINDOW FACES	NO INTERNAL SHADING
N	23	27	31	35	39	43		19	21	23	25	27	29		17	18	19	20	21	22
NE AND NW	38	42	46	50	54	58		32	34	36	38	40	42		29	30	31	32	33	34
E AND W	49	53	57	61	65	69		41	43	45	47	49	51		37	38	39	40	41	42
SE AND SW	44	48	52	56	60	64		37	39	41	43	45	47		33	34	35	36	37	38
S	31	35	39	43	47	51		26	28	30	32	34	36		23	24	25	26	27	28
	DRAPERIES OR VENETIAN BLINDS	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!			2	4	6	8	10			1	2	3	4	5
N	14	18	22	26	30	34		12	14	16	18	20	22		10	11	12	13	14	15
NE AND NW	23	27	31	35	39	43		20	22	24	26	28	30		17	18	19	20	21	22
E AND W	29	33	37	41	45	49		26	28	30	32	34	36		22	23	24	25	26	27
SE AND SW	26	30	34	38	42	46		23	25	27	29	31	33		20	21	22	23	24	25
S	19	23	27	31	35	39		16	18	20	22	24	26		14	15	16	17	18	19
	ROLLER SHADES – HALF DRAWN	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!			2	4	6	8	10			1	2	3	4	5
N	17	21	25	29	33	37		16	18	20	22	24	26		14	15	16	17	18	19
NE AND NW	28	32	36	40	44	48		26	28	30	32	34	36		23	24	25	26	27	28
E AND W	36	40	44	48	52	56		34	36	38	40	42	44		30	31	32	33	34	35
SE AND SW	33	37	41	45	49	53		30	32	34	36	38	40		27	28	29	30	31	32
S	23	27	31	35	39	43		21	23	25	27	29	31		19	20	21	22	23	24
TINTED (HEAT ABSORBING) GLASS		4	8	12	16	20			2	4	6	8	10			1	2	3	4	5
	SINGLE PANE	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!		DOUBLE PANE AND SINGLE PANE LOW E COATING	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!		TRIPLE PANE AND DOUBLE PANE LOW E COATING	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!
DESIGN TEMP DIFFERENCE	10	14	18	22	26	30		10	12	14	16	18	20		10	11	12	13	14	15
DIRECTION WINDOW FACES	NO INTERNAL SHADING	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!			2	4	6	8	10			1	2	3	4	5
N	16	20	24	28	32	36		12	14	16	18	20	22		9	10	11	12	13	14
NE AND NW	26	30	34	38	42	46		20	22	24	26	28	30		15	16	17	18	19	20
E AND W	34	38	42	46	50	54		26	28	30	32	34	36		19	20	21	22	23	24
SE AND SW	31	35	39	43	47	51		23	25	27	29	31	33		18	19	20	21	22	23
S	21	25	29	33	37	41		16	18	20	22	24	26		12	13	14	15	16	17
	DRAPERIES OR VENETIAN BLINDS	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!			2	4	6	8	10			1	2	3	4	5
N	12	16	20	24	28	32		9	11	13	15	17	19		6	7	8	9	10	11
NE AND NW	20	24	28	32	36	40		15	17	19	21	23	25		10	11	12	13	14	15
E AND W	26	30	34	38	42	46		19	21	23	25	27	29		13	14	15	16	17	18
SE AND SW	23	27	31	35	39	43		17	19	21	23	25	27		11	12	13	14	15	16
S	16	20	24	28	32	36		12	14	16	18	20	22		8	9	10	11	12	13
	ROLLER SHADES – HALF DRAWN	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!			2	4	6	8	10			1	2	3	4	5
N	14	18	22	26	30	34		10	12	14	16	18	20		7	8	9	10	11	12
NE AND NW	23	27	31	35	39	43		17	19	21	23	25	27		12	13	14	15	16	17
E AND W	30	34	38	42	46	50		22	24	26	28	30	32		16	17	18	19	20	21
SE AND SW	27	31	35	39	43	47		19	21	23	25	27	29		14	15	16	17	18	19
S	19	23	27	31	35	39		14	16	18	20	22	24		10	11	12	13	14	15
REFLECTIVE COATED GLASS		4	8	12	16	20			2	4	6	8	10			1	2	3	4	5
	SINGLE PANE	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!		DOUBLE PANE AND SINGLE PANE LOW E COATING	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!		TRIPLE PANE AND DOUBLE PANE LOW E COATING	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!
DESIGN TEMP DIFFERENCE	10	14	18	22	26	30		10	12	14	16	18	20		10	11	12	13	14	15
DIRECTION WINDOW FACES	NO INTERNAL SHADING	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!			2	4	6	8	10			1	2	3	4	5
N	14	18	22	26	30	34		10	12	14	16	18	20		6	7	8	9	10	11
NE AND NW	23	27	31	35	39	43		16	18	20	22	24	26		10	11	12	13	14	15
E AND W	30	34	38	42	46	50		21	23	25	27	29	31		13	14	15	16	17	18
SE AND SW	27	31	35	39	43	47		19	21	23	25	27	29		11	12	13	14	15	16
S	19	23	27	31	35	39		13	15	17	19	21	23		8	9	10	11	12	13
	DRAPERIES OR VENETIAN BLINDS	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!			2	4	6	8	10			1	2	3	4	5
N	11	15	19	23	27	31		8	10	12	14	16	18		5	6	7	8	9	10
NE AND NW	19	23	27	31	35	39		13	15	17	19	21	23		8	9	10	11	12	13
E AND W	24	28	32	36	40	44		18	20	22	24	26	28		10	11	12	13	14	15
SE AND SW	22	26	30	34	38	42		16	18	20	22	24	26		10	11	12	13	14	15
S	15	19	23	27	31	35		11	13	15	17	19	21		7	8	9	10	11	12
	ROLLER SHADES – HALF DRAWN	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!			2	4	6	8	10			1	2	3	4	5
N	12	16	20	24	28	32		9	11	13	15	17	19		5	6	7	8	9	10
NE AND NW	20	24	28	32	36	40		14	16	18	20	22	24		9	10	11	12	13	14
E AND W	26	30	34	38	42	46		19	21	23	25	27	29		11	12	13	14	15	16
SE AND SW	24	28	32	36	40	44		17	19	21	23	25	27		10	11	12	13	14	15
S	17	21	25	29	33	37		12	14	16	18	20	22		7	8	9	10	11	12

## TABLE 3F
TABLE 3F
GLASS HEAT TRANSFER MULTIPLIERS (COOLING)
SKYLIGHTS
CLEAR GLASS OR PLASTIC
	SINGLE PANE					DOUBLE PANE AND SINGLE PANE LOW E COATING
DESIGN TEMP DIFFERENCE	10	15	20	25	30	35		10	15	20	25	30	35
	INCLINATION = 60°
DIRECTION WINDOW FACES
NO EXTERNAL SHADE SCREEN	100	105	111	116	122	127		86	89	92	94	97	100
NE AND NW	128	133	139	144	150	155		110	113	116	118	121	124
E AND W	150	155	161	166	172	177		128	131	134	136	139	142
SE AND SW	141	146	152	157	163	168		121	124	127	129	132	135
S	115	120	126	131	137	142		99	102	105	107	110	113
	INCLINATION = 45°	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!			3	6	8	11	14
N	129	134	140	145	151	156		112	115	118	120	123	126
NE AND NW	153	158	164	169	175	180		132	135	138	140	143	146
E AND W	170	175	181	186	192	197		146	149	152	154	157	160
SE AND SW	163	168	174	179	185	190		140	143	146	148	151	154
S	141	146	152	157	163	168		122	125	128	130	133	136
	INCLINATION = 30°	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!			3	6	8	11	14
N	150	155	161	166	172	177		130	133	136	138	141	144
NE AND NW	167	172	178	183	189	194		144	147	150	152	155	158
E AND W	179	184	190	195	201	206		154	157	160	162	165	168
SE AND SW	174	179	185	190	196	201		150	153	156	158	161	164
S	159	164	170	175	181	186		137	140	143	145	148	151
	INCLINATION = 0°
HORIZONTAL	160	164	168	172	176	180		139	141	143	145	147	149

TINTED (HEAT ABSORBING) GLASS OR OPAQUE PLASTIC SKYLIGHTS
	SINGLE PANE					DOUBLE PANE AND SINGLE PANE LOW E COATING
DESIGN TEMP DIFFERENCE	10	15	20	25	30	35		10	15	20	25	30	35
	INCLINATION = 60°
DIRECTION WINDOW FACES
N	70	75	81	86	92	97		55	58	60	63	66	69
NE AND NW	90	95	101	106	112	117		70	73	75	78	81	84
E AND W	106	111	117	122	128	133		81	84	86	89	92	95
SE AND SW	99	104	110	115	121	126		76	79	81	84	87	90
S	80	85	91	96	102	107		63	66	68	71	74	77
	INCLINATION = 45°	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!			3	5	8	11	14
N	91	96	102	107	113	118		71	74	76	79	82	85
NE AND NW	107	112	118	123	129	134		83	86	88	91	94	97
E AND W	120	125	131	136	142	147		93	96	98	101	104	107
SE AND SW	114	119	125	130	136	141		88	91	93	96	99	102
S	99	104	110	115	121	126		78	81	83	86	89	92
	INCLINATION = 30°	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!			3	5	8	11	14
N	105	110	116	121	127	132		83	86	88	91	94	97
NE AND NW	117	122	128	133	139	144		92	95	97	100	103	106
E AND W	126	131	137	142	148	153		98	101	103	106	109	112
SE AND SW	122	127	133	138	144	149		95	98	100	103	106	109
S	111	116	122	127	133	138		88	91	93	96	99	102
	INCLINATION = 0°
HORIZONTAL	112	116	120	124	128	132		89	91	93	95	97	99
REFLECTIVE COATED SKYLIGHTS
	SINGLE PANE					DOUBLE PANE AND SINGLE PANE LOW E COATING
DESIGN TEMP DIFFERENCE	10	15	20	25	30	35		10	15	20	25	30	35
	INCLINATION = 60°
DIRECTION WINDOW FACES
N	52	58	63	69	74	80		41	44	46	49	52	55
NE AND NW	70	76	81	87	92	98		53	56	58	61	64	67
E AND W	83	89	94	100	105	111		62	65	67	70	73	76
SE AND SW	77	83	88	94	99	105		57	60	62	65	68	71
S	61	67	72	78	83	89		47	50	52	55	58	61
	INCLINATION = 45°	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!			3	5	8	11	14
N	65	71	76	82	87	93		51	54	56	59	62	65
NE AND NW	77	83	88	94	99	105		60	63	65	68	71	74
E AND W	85	91	96	102	107	113		67	70	72	75	78	81
SE AND SW	82	88	93	99	104	110		64	67	69	72	75	78
S	71	77	82	88	93	99		56	59	61	64	67	70
	INCLINATION = 30°	#VALUE!	#VALUE!	#VALUE!	#VALUE!	#VALUE!			3	5	8	11	14
N	76	82	87	93	98	104		60	63	65	68	71	74
NE AND NW	85	91	96	102	107	113		66	69	71	74	77	80
E AND W	92	98	103	109	114	120		71	74	76	79	82	85
SE AND SW	89	95	100	106	111	117		69	72	74	77	80	83
S	81	87	92	98	103	109		63	66	68	71	74	77
	INCLINATION = 0°
HORIZONTAL	80	84	88	92	96	100		64	66	68	70	72	74

## TABLE 4
NO. 10	WOOD DOORS	SUMMER TEMPERATURE DESIGN DIFFERENCE AND DAILY TEMPERATURE RANGE
		10		15			20			25		30	35	U
		L	M	L	M	H	L	M	H	M	H	H	H
		HTM (BTUH PER SQUARE FOOT)
A.	HOLLOW CORE	9.9	7.6	12.7	10.4	7.6	15.5	13.2	10.4	16.0	13.2	16.0	18.8	.560
B.	HOLLOW CORE & WOOD STORM	5.8	4.5	7.5	6.1	4.5	9.1	7.8	6.1	9.4	7.8	9.4	11.1	.330
C.	HOLLOW CORE & METAL STORM	6.3	4.9	8.1	6.7	4.9	9.9	8.5	6.7	10.3	8.5	10.3	12.1	.360
D.	SOLID CORE	8.1	6.3	10.4	8.6	6.3	12.7	10.9	8.6	13.2	10.9	13.2	15.5	.460
E.	SOLID CORE & WOOD STORM	5.1	3.9	6.6	5.4	3.9	8.0	6.8	5.4	8.3	6.8	8.3	9.7	.290
F.	SOLID CORE & METAL STORM	5.6	4.4	7.2	6.0	4.4	8.8	7.6	6.0	9.2	7.6	9.2	10.8	.320
G.	PANEL	11.8	9.1	15.1	12.5	9.1	18.5	15.8	12.5	19.2	15.8	19.2	22.5	.670
H.	PANEL & WOOD STORM	6.3	4.9	8.1	6.7	4.9	9.9	8.5	6.7	10.3	8.5	10.3	12.1	.360
I.	PANEL & METAL STORM	7.2	5.6	9.3	7.6	5.6	11.3	9.7	7.6	11.7	9.7	11.7	13.8	.410
NO. 11	METAL DOORS	SUMMER TEMPERATURE DESIGN DIFFERENCE AND DAILY TEMPERATURE RANGE
		10		15			20			25		30	35	U
		L	M	L	M	H	L	M	H	M	H	H	H
		HTM (BTUH PER SQUARE FOOT)
A.	FIBERGLASS CORE	10.4	8.0	13.3	11.0	8.0	16.3	13.9	11.0	16.9	13.9	16.9	19.8	.590
B.	FIBERGLASS CORE & STORM	6.5	5.0	8.3	6.8	5.0	10.1	8.7	6.8	10.5	8.7	10.5	12.3	.367
C.	POLYSTYRENE CORE	8.3	6.4	10.6	8.7	6.4	13.0	11.1	8.7	13.4	11.1	13.4	15.8	.470
D.	POLYSTYRENE CORE & STORM	5.6	4.3	7.2	5.9	4.3	8.7	7.5	5.9	9.1	7.5	9.1	10.7	.317
E.	URETHANE CORE	3.3	2.6	4.3	3.5	2.6	5.2	4.5	3.5	5.4	4.5	5.4	6.4	.190
F.	URETHANE CORE & STORM	3.0	2.3	3.8	3.2	2.3	4.7	4.0	3.2	4.9	4.0	4.9	5.7	.170
NO. 12	WOOD FRAME EXTERIOR WALLS WITH SHEATHING AND SIDING OR BRICK VENEER OR OTHER EXTERIOR FINISH	10		15			20			25		30	35	U
		L	M	L	M	H	L	M	H	M	H	H	H
		HTM (BTUH PER SQUARE FOOT)
A.	NONE ½” GYPSUM BOARD (R0.5)	4.8	3.7	6.1	5.0	3.7	7.5	6.4	5.0	7.8	6.4	7.8	9.1	.271
B.	NONE ½” ASPHAULT BOARD (R1.3)	3.8	3.0	4.9	4.0	3.0	6.0	5.1	4.0	6.2	5.1	6.2	7.3	.217
C.	R11 ½” GYPSUM BOARD (R0.5)	1.6	1.2	2.0	1.7	1.2	2.5	2.1	1.7	2.6	2.1	2.6	3.0	.090
D.	R11 ½” ASPHAULT BOARD (R1.3)	1.4	1.1	1.8	1.5	1.1	2.2	1.9	1.5	2.3	1.9	2.3	2.7	.080
	R11 ½” BEAD BOARD (R1.8)
	R13 ½” GYPSUM BOARD (R0.5)
E.	R11 ½” POLY BOARD(R2.5)	1.3	1.0	1.7	1.4	1.0	2.1	1.8	1.4	2.1	1.8	2.1	2.5	.075
	R11 ¾” EXTR POLYBOARD (R2.5)
	R13 ½” ASPHALT BOARD (R1.3)
	R13 R13 ½” BEAD BOARD (R1.8)
F.	R11 1” BEAD BOARD (R3.6)	1.2	1.0	1.6	1.3	1.0	1.9	1.7	1.3	2.0	1.7	2.0	2.4	.070
	R11 ¾” EXTR POLY BOARD (R3.8)
	R13 ½” EXTR POLY BOARD (R2.5)
	R13 ¾” BEAD BOARD (R2.7)
G.	R13 ¾” EXTR POLY BOARD (R3.8)	1.1	.9	1.5	1.2	.9	1.8	1.5	1.2	1.9	1.5	1.9	2.2	.065
	R13 1” BEAD BOARD (R3.6)
H.	R11 1” EXTR POLY BOARD (R5.0)	1.1	.8	1.4	1.1	.8	1.7	1.4	1.1	1.7	1.4	1.7	2.0	.060
	R13 1” EXTR POLY BOARD (R5.0)
	R19 ½” GYPSUM BOARD (R0.5)
I.	R19 ½” ASPHALT BOARD (R1.3)	1.0	.7	1.2	1.0	.7	1.5	1.3	1.0	1.6	1.3	1.6	1.8	.055
	R19 ½” BEAD BOARD (R1.8)
J.	R11 R8 SHEATHING	.9	.7	1.1	.9	.7	1.4	1.2	.9	1.4	1.2	1.4	1.7	.050
	R13 R8 SHEATHING
	R19 ½” OR ¾” EXTR POLY BOARD
	R19 ¾” OR 1’ BEAD BOARD
K.	R19 1” EXTR POLY BOARD (R5.0)	.8	.6	1.0	.8	.6	1.2	1.1	.8	1.3	1.1	1.3	1.5	.045
L.	R19 R8 SHEATHING	.7	.5	.9	.7	.5	1.1	.9	.7	1.1	.9	1.1	1.3	.040
NO. 13	PARTITIONS BETWEEN CONDITIONED AND UNCONDITIONED SPACE – WOOD FRAME PARTITIONS	10		15			20			25		30	35	U
		L	M	L	M	H	L	M	H	M	H	H	H

A.	NONE ½” GYPSUM BOARD (R0.5)	2.4	1.4	3.8	2.7	1.4	5.1	4.1	2.7	5.4	4.1	5.4	6.8	.271
B.	NONE ½” ASPHAULT BOARD (R1.3)	2.0	1.1	3.0	2.2	1.1	4.1	3.3	2.2	4.3	3.3	4.3	5.4	.217
C.	R11 ½” GYPSUM BOARD (R0.5)	.8	.4	1.3	.9	.4	1.7	1.3	.9	1.8	1.3	1.8	2.2	.090
D.	R11 ½” ASPHAULT BOARD (R1.3)	.7	.4	1.1	.8	.4	1.5	1.2	.8	1.6	1.2	1.6	2.0	.080
	R11 ½” BEAD BOARD (R1.8)
	R13 ½” GYPSUM BOARD (R0.5)
E.	R11 ½” POLY BOARD(R2.5)	.7	.4	1.0	.8	.4	1.4	1.1	.8	1.5	1.1	1.5	1.9	.075
	R11 ¾” EXTR POLYBOARD (R2.5)
	R13 ½” ASPHALT BOARD (R1.3)
	R13 R13 ½” BEAD BOARD (R1.8)
F.	R11 1” BEAD BOARD (R3.6)	.6	.4	1.0	.7	.4	1.0	1.0	.7	1.4	1.0	1.4	1.8	.070
	R11 ¾” EXTR POLY BOARD (R3.8)
	R13 ½” EXTR POLY BOARD (R2.5)
	R13 ¾” BEAD BOARD (R2.7)
G.	R13 ¾” EXTR POLY BOARD (R3.8)	.6	.3	.9	.6	.3	3.0	1.0	.6	1.3	1.0	1.3	1.6	.065
	R13 1” BEAD BOARD (R3.6)
H.	R11 1” EXTR POLY BOARD (R5.0)	.5	.3	.8	.6	.3	1.2	.9	.6	1.2	.9	1.2	1.5	.060
	R13 1” EXTR POLY BOARD (R5.0)
	R19 ½” GYPSUM BOARD (R0.5)
I.	R19 ½” ASPHALT BOARD (R1.3)	.5	.3	.8	.5	.3	1.1	.8	.5	1.1	.8	1.1	1.4	.055
	R19 ½” BEAD BOARD (R1.8)
J.	R11 R8 SHEATHING	.4	.2	.7	.5	.2	1.0	.7	.5	1.0	.7	1.0	1.2	.050
	R13 R8 SHEATHING
	R19 ½” OR ¾” EXTR POLY BOARD
	R19 ¾” OR 1’ BEAD BOARD
K.	R19 1” EXTR POLY BOARD (R5.0)	.4	.2	.6	.4	.2	.9	.7	.4	.9	.7	.9	1.1	.045
L.	R19 R8 SHEATHING	.4	.2	.6	.4	.2	.8	.6	.4	.8	.6	.8	1.0	.040
NO. 13a	PARTITIONS BETWEEN CONDITIONED & UNCONDITIONED SPACE. BRICK OR BLOCK PARTITIONS	10		15			20			25		30	35	U
		L	M	L	M	H	L	M	H	M	H	H	H
		HTM (BTUH PER SQUARE FOOT)
A.	8” OR 12” BLOCK, NO INSUL., UNFINISHED	1.3	.0	3.8	1.8	.0	6.4	4.3	1.8	6.9	4.3	6.9	9.4	.510
B.	8” OR 12” BLOCK + R5	.4	.0	1.1	.5	.0	1.8	1.2	.5	1.9	1.2	1.9	2.7	.144
C.	8” OR 12” BLOCK + R11	.2	.0	.6	.3	.0	1.0	.7	.3	1.0	.7	1.0	1.4	.077
D.	8” OR 12” BLOCK + R19	.1	.0	.4	.2	.0	.6	.4	.2	.6	.4	.6	.9	.048
E.	4” BRICK, 8” BLOCK, NO INSUL	1.0	.0	3.0	1.4	.0	5.0	3.4	1.4	5.4	3.4	5.4	7.4	.400
F.	4” BRICK, 8” BLOCK + R5	.3	.0	1.0	.5	.0	1.7	1.1	.5	1.8	1.1	1.8	2.5	.133
G.	4” BRICK, 8” BLOCK + R11	.2	.0	.6	.3	.0	.9	.6	.3	1.0	.6	1.0	1.4	.074
H.	4” BRICK, 8” BLOCK + R19	.1	.0	.4	.2	.0	.6	.4	.2	.6	.4	.6	.9	.047
NO. 14	MASONRY WALLS, BLOCK OR BRICK FINISHED OR UNFINISHED – ABOVE GRADE	10		15			20			25		30	35	U
		L	M	L	M	H	L	M	H	M	H	H	H
		HTM (BTUH PER SQUARE FOOT)
A.	8” OR 12” BLOCK, NO INSUL., UNFINISHED	5.3	3.2	7.8	5.8	3.2	10.4	8.3	5.8	10.9	8.3	10.9	13.4	.510
B.	8” OR 12” BLOCK + R5	1.5	.9	2.2	1.6	.9	2.9	2.3	1.6	3.1	2.3	3.1	3.8	.144
C.	8” OR 12” BLOCK + R11	.8	.5	1.2	.9	.5	1.6	1.3	.9	1.6	1.3	1.6	2.0	.077
D.	8” OR 12” BLOCK + R19	.5	.3	.7	.5	.3	1.0	.8	.5	1.0	.8	1.0	1.3	.048
E.	4” BRICK, 8” BLOCK, NO INSUL	4.1	2.5	6.1	4.5	2.5	8.1	6.5	4.5	8.5	6.5	8.5	10.5	.400
F.	4” BRICK, 8” BLOCK + R5	1.4	.8	2.0	1.5	.8	2.7	2.2	1.5	2.8	2.2	2.8	3.5	.133
G.	4” BRICK, 8” BLOCK + R11	.8	.5	1.1	.8	.5	1.5	1.2	.8	1.6	1.2	1.6	1.9	.074
H.	4” BRICK, 8” BLOCK + R19	.5	.3	.7	.5	.3	1.0	.8	.5	1.0	.8	1.0	1.2	.047
NO. 15	MASONRY WALLS, BLOCK OR BRICK, BELOW GRADE	10		15			20			25		30	35	U
		L	M	L	M	H	L	M	H	M	H	H	H
		HTM (BTUH PER SQUARE FOOT)
ALL		.0
NO. 16	CEILINGS UNDER A VENTILATED ATTIC SPACE (LIGHT COLORED ROOF)	10		15			20			25		30	35	U
		L	M	L	M	H	L	M	H	M	H	H	H
		HTM (BTUH PER SQUARE FOOT)
A.	NO INSULATION	13.1	11.4	15.3	13.5	11.4	17.5	15.7	13.5	17.9	15.7	17.9	20.1	.437
B.	R7 INSULATION	3.4	2.9	3.9	3.5	2.9	4.5	4.0	3.5	4.6	4.0	4.6	5.2	.112
C.	R11 INSULATION	2.5	2.2	2.9	2.6	2.2	3.3	3.0	2.6	3.4	3.0	3.4	3.8	.083
D.	R19 INSULATION	1.6	1.4	1.9	1.6	1.4	2.1	1.9	1.6	2.2	1.9	2.2	2.4	.053
E.	R22 INSULATION	1.4	1.2	1.7	1.5	1.2	1.9	1.7	1.5	2.0	1.7	2.0	2.2	.048
F.	R26 INMSULATION	1.1	1.0	1.3	1.2	1.0	1.5	1.4	1.2	1.6	1.4	1.6	1.7	.038
G.	R30 INSULATION	1.0	.9	1.2	1.0	.9	1.3	1.2	1.0	1.4	1.2	1.4	1.5	.033
H.	R38 INSULATION	.8	.7	.9	.8	.7	1.0	.9	.8	1.1	.9	1.1	1.2	.026
I.	R44 INSULATION	.7	.6	.8	.7	.6	.9	.8	.7	.9	.8	.9	1.1	.023
J.	R57 INSULATION	.5	.4	.6	.5	.4	.7	.6	.5	.7	.6	.7	.8	.017
K.	WOOD DECKING, NO INSULATION	8.6	7.5	10.0	8.9	7.4	11.4	10.3	8.9	11.8	10.3	11.8	13.2	.287
NO. 16a	CEILINGS UNDER A VENTILATED ATTIC SPACE (DARK COLORED ROOF)	10		15			20			25		30	35	U
		L	M	L	M	H	L	M	H	M	H	H	H
		HTM (BTUH PER SQUARE FOOT)
A.	NO INSULATION	16.6	14.9	18.8	17.0	14.9	21.0	19.2	17.0	21.4	19.2	21.4	23.6	.437
B.	R7 INSULATION	4.3	3.8	4.8	4.4	3.8	5.4	4.9	4.4	5.5	4.9	5.5	6.0	.112
C.	R11 INSULATION	3.2	2.8	3.6	3.2	2.8	4.0	3.7	3.2	4.1	3.7	4.1	4.5	.083
D.	R19 INSULATION	2.0	1.8	2.3	2.1	1.8	2.5	2.3	2.1	2.6	2.3	2.6	2.9	.053
E.	R22 INSULATION	1.8	1.6	2.1	1.9	1.6	2.3	2.1	1.9	2.4	2.1	2.4	2.6	.048
F.	R26 INMSULATION	1.4	1.3	1.6	1.5	1.3	1.8	1.7	1.5	1.9	1.7	1.9	2.1	.038
G.	R30 INSULATION	1.3	1.1	1.4	1.3	1.1	1.6	1.5	1.3	1.6	1.5	1.6	1.8	.033
H.	R38 INSULATION	1.0	.9	1.1	1.0	.9	1.2	1.1	1.0	1.3	1.1	1.3	1.4	.026
I.	R44 INSULATION	.9	.8	1.0	.9	.8	1.1	1.0	.9	1.1	1.0	1.1	1.2	.023
J.	R57 INSULATION	.6	.6	.7	.7	.6	.8	.7	.7	.8	.7	.8	.9	.017
K.	WOOD DECKING, NO INSULATION	10.9	9.8	12.3	11.2	9.8	13.8	12.6	11.2	14.0	12.6	14.0	15.5	.287
NO. 17	ROOF ON EXPOSED BEAMS OR RAFTERS (LIGHT COLORED ROOF)	10		15			20			25		30	35	U
		L	M	L	M	H	L	M	H	M	H	H	H
		HTM (BTUH PER SQUARE FOOT)
A.	1 ½” WOOD DECKING, NO INSULATION	8.8	7.6	10.3	9.1	7.6	11.8	10.6	9.1	12.1	10.6	12.1	13.5	.294
B.	1 ½” WOOD DECKING (R4)	4.2	3.6	4.9	4.3	3.6	5.6	5.0	4.3	5.7	5.0	5.7	6.4	.140
C.	1 ½” WOOD DECKING (R5)	3.6	3.1	4.2	3.7	3.1	4.8	4.3	3.7	4.9	4.3	4.9	5.5	.119
D.	1 ½” WOOD DECKING (R6)	3.2	2.8	3.7	3.3	2.8	4.2	3.8	3.3	4.3	3.8	4.3	4.9	.106
E.	1 ½” WOOD DECKING (R8)	2.6	2.3	3.1	2.7	2.3	3.5	3.2	2.7	3.6	3.2	3.6	4.0	.088
F.	2” SHREDDED WOOD PLANKS	6.2	5.4	7.2	6.4	5.4	8.3	7.5	6.4	8.5	7.5	8.5	9.5	.207
G.	3” SHREDDED WOOD PLANKS	4.6	4.0	5.4	4.3	4.0	6.2	5.5	4.8	6.3	5.5	6.3	7.1	.154
H.	1 ½” FIBER BOARD INSUL	5.1	4.4	5.9	5.2	4.4	6.8	6.1	5.2	6.9	6.1	6.9	7.8	.169
I.	2” FIBER BOARD INSUL	4.0	3.5	4.7	4.2	3.5	5.4	4.9	4.2	5.5	4.9	5.5	6.2	.135
J.	3” FIBER BOARD INSUL	2.9	2.5	3.4	3.0	2.5	3.9	3.5	3.0	4.0	3.5	4.0	4.5	.097
K.	1 ½” WOOD DECKING (R13)	1.8	1.6	2.1	1.9	1.6	2.4	2.2	1.9	2.5	2.2	2.5	2.8	.060
L.	1 ½” WOOD DECKING (R19)	1.2	1.1	1.4	1.3	1.1	1.6	1.5	1.3	1.7	1.5	1.7	1.9	.041
NO. 17a	ROOF ON EXPOSED BEAMS OR RAFTERS (DARK COLORED ROOF)	10		15			20			25		30	35	U
		L	M	L	M	H	L	M	H	M	H	H	H
		HTM (BTUH PER SQUARE FOOT)
A.	1 ½” WOOD DECKING, NO INSULATION	11.2	10.0	12.6	11.5	10.0	14.1	12.9	11.5	14.4	12.9	14.4	15.9	.294
B.	1 ½” WOOD DECKING (R4)	5.3	4.8	6.0	5.5	4.8	6.7	6.2	5.5	6.9	6.2	6.9	7.6	.140
C.	1 ½” WOOD DECKING (R5)	4.5	4.0	5.1	4.6	4.0	5.7	5.2	4.6	5.8	5.2	5.8	6.4	.119
D.	1 ½” WOOD DECKING (R6)	4.0	3.6	4.6	4.1	3.6	5.1	4.7	4.1	5.2	4.7	5.2	5.7	.106
E.	1 ½” WOOD DECKING (R8)	3.3	3.0	3.8	3.4	3.0	4.2	3.9	3.4	4.3	3.9	4.3	4.8	.088
F.	2” SHREDDED WOOD PLANKS	7.9	7.0	8.9	8.1	7.0	9.9	9.1	8.1	10.1	9.1	10.1	11.2	.207
G.	3” SHREDDED WOOD PLANKS	5.9	5.2	6.6	6.0	5.2	7.4	6.8	6.0	7.5	6.8	7.5	8.3	.154
H.	1 ½” FIBER BOARD INSUL	6.4	5.7	7.3	6.6	5.7	8.1	7.4	6.6	8.3	7.4	8.3	9.1	.169
I.	2” FIBER BOARD INSUL	5.1	4.6	5.8	5.3	4.6	6.5	5.9	5.3	6.6	5.9	6.6	7.3	.136
J.	3” FIBER BOARD INSUL	3.7	3.3	4.2	3.8	3.3	4.7	4.3	3.8	4.8	4.3	4.8	5.2	.097
K.	1 ½” WOOD DECKING (R13)	2.3	2.0	2.6	2.3	2.0	2.9	2.6	2.3	2.9	2.6	2.9	3.2	.060
L.	1 ½” WOOD DECKING (R19)	1.6	1.4	1.8	1.6	1.4	2.0	1.8	1.6	2.0	1.8	2.0	2.2	.041
NO. 18	ROOF-CEILING COMBINATION – LIGHT COLORED ROOF	10		15			20			25		30	35	U
		L	M	L	M	H	L	M	H	M	H	H	H
		HTM (BTUH PER SQUARE FOOT)
A.	NO INSULATION	8.6	7.5	10.0	8.9	7.5	11.5	10.3	8.9	11.8	10.3	11.8	13.2	.287
B.	R11 BATTS	2.2	1.9	2.5	2.2	1.9	2.9	2.6	2.2	3.0	2.6	3.0	3.3	.072
C.	R19 BATTS	1.5	1.3	1.7	1.5	1.3	2.0	1.8	1.5	2.0	1.8	2.0	2.3	.049
D.	R22 BATTS (2” X 8” RAFTERS)	1.3	1.2	1.6	1.4	1.2	1.8	1.6	1.4	1.8	1.6	1.8	2.1	.045
E.	R26 BATTS (2” X 8” RAFTERS)	1.2	1.0	1.4	1.2	1.0	1.6	1.4	1.2	1.6	1.4	1.6	1.8	.040
F.	R30 BATTS (2” X 10” RAFTERS)	1.0	.9	1.2	1.1	.9	1.4	1.3	1.1	1.4	1.3	1.4	1.6	.035
NO. 18a	ROOF-CEILING COMBINATION – DARK COLORED ROOF	10		15			20			25		30	35	U
		L	M	L	M	H	L	M	H	M	H	H	H
		HTM (BTUH PER SQUARE FOOT)
A.	NO INSULATION	10.9	9.8	12.3	11.2	9.8	13.8	12.6	11.2	14.1	12.6	14.1	15.5	.287
B.	R11 BATTS	2.7	2.4	3.1	2.8	2.4	3.5	3.2	2.8	3.5	3.2	3.5	3.9	.072
C.	R19 BATTS	1.9	1.7	2.1	1.9	1.7	2.4	1.9	1.9	2.4	2.2	2.4	2.6	.049
D.	R22 BATTS (2” X 8” RAFTERS)	1.7	1.5	1.9	1.8	1.5	2.2	1.8	1.8	2.2	2.0	2.2	2.4	.045
E.	R26 BATTS (2” X 8” RAFTERS)	1.5	1.4	1.7	1.6	1.4	1.9	1.6	1.6	2.0	1.8	2.0	2.2	.040
F.	R30 BATTS (2” X 10” RAFTERS)	1.3	1.2	1.5	1.4	1.2	1.7	1.4	1.4	1.7	1.5	1.7	1.9	.035
NO. 19	FLOORS OVER A BASEMENT OR ENCLOSED CRAWL SPACE	10		15			20			25		30	35	U
		L	M	L	M	H	L	M	H	M	H	H	H
		HTM (BTUH PER SQUARE FOOT)
ALL		.0
NO. 20	FLOORS OVER AN OPEN CRAWL SPACE OR GARAGE	10		15			20			25		30	35	U
		L	M	L	M	H	L	M	H	M	H	H	H
		HTM (BTUH PER SQUARE FOOT)
A.	HARDWOOD FLOOR, NO INSULATION	3.5	1.9	5.4	3.9	1.9	7.3	5.8	3.9	7.7	5.8	7.7	9.6	.386
B.	HARDWOOD FLOOR (R11)	.8	.4	1.2	.8	.4	1.6	1.3	.8	1.7	1.3	5.8	2.1	.084
C.	HARDWOOD FLOOR (R13)	.7	.4	1.1	.8	.4	1.4	1.1	.8	1.5	1.1	1.3	1.9	.076
D.	HARDWOOD FLOOR (R19)	.5	.3	.8	.5	.3	1.0	.8	.5	1.1	.8	1.1	1.3	.054
E.	HARDWOOD FLOOR (R30)	.3	.2	.5	.4	.2	.7	.6	.4	.8	.6	.8	.9	.037
F.	CARPET FLOOR NO INSULATION	2.3	1.3	3.5	2.5	1.3	4.8	3.8	2.5	.6	3.8	.6	6.3	.253
G.	CARPET FLOOR (R11)	.7	.3	1.0	.8	.4	1.4	1.1	.8	3.8	1.1	3.8	1.9	.075
H.	CARPET FLOOR (R13)	.6	.3	1.0	.7	.3	1.3	1.0	.7	1.1	1.0	1.1	1.7	.068
I.	CARPET FLOOR (R19)	.4	.2	.7	.5	.2	.9	.7	.5	1.0	.7	1.0	1.2	.050
J.	CARPET FLOOR (R30)	.3	.2	.5	.4	.2	.7	.5	.4	.7	.5	.7	.9	.035
NO. 21-23	BASEMENT FLOORS, CONCRETE SLAB ON GRADE	10		15			0.4			0.7		0.5	35	U
		L	M	L	M	H	L	M	H	M	H	H	H
		HTM (BTUH PER SQUARE FOOT)
ALL		.0

## TABLE 5
INFILTRATION EVALUATION					DETAILED INFILTRATION ESTIMATE
				STEP 1: CALCULATE THE LEAKAGE AREA (SQ. IN.) FOR THE ENTIRE HOUSE.
WINTER AIR CHANGES PER HOUR					LEAKAGE AREA FACTORS (AF)			“A” ENTER (AF) VALUE	“B” ENTER AREA OR COUNT	“C” MULTIPLY (AF) X AREA
FLOOR AREA	900 OR LESS	900-1500	1500-2100	OVER 2100
BEST	0.4	0.4	0.3	0.3				BEST	AVERAGE	POOR
AVERAGE	1.2	1	0.8	0.7			EXTERIOR WALLS
POOR	2.2	1.6	1.2	1			WOOD FRAMING & EXTERIOR SIDING	.007	.038	.068
FOR EACH ADDITIONAL FIREPLACE ADD: BEST 0.1 AVERAGE 0.2 POOR 0.6					SLATS, BOARDS, PANELS	.007	.025	.044
				MASONRY WALLS, ANY SIDING	.009	.032	.054
SUMMER AIR CHANGES PER HOUR
FLOOR AREA	900 OR LESS	900-1500	1500-2100	OVER 2100			WINDOWS & SLIDING GLASS DOORS
BEST	0.2	0.2	0.2	0.2			WITH STORM	.015	.030	.040
AVERAGE	0.5	0.5	0.4	0.4			NO STORM	.020	.050	.080
POOR	0.8	0.7	0.6	0.5			JALOUSIE WINDOWS WITH STORM	.000	.000	.080
				JALOUSIE WINDOWS NO STORM	.000	.000	.150

				WOOD/METAL AND FRENCH DOORS
				WITH STORM	.040	.080	.120
				NO STORM	.060	.120	.240

				ENVELOPE PENETRATIONS
				RECESSED LIGHT FIXTURES	1.000	.000	2.000
				PIPE PENETRATIONS	.160	.000	.930
				DUCT PENETRATIONS	.250	.000	3.700
				WINDOW OR THRU WALL EQUIPMENT	.000	2.000	4.000

				VENTS AND EXHAUSTS
				KITCHEN FAN	.800	.000	6.000
				BATHROOM FAN	1.700	.000	3.100
				DRYER VENT	.470	.000	4.000

				FURNACE, DUCTS AND WATER HEATER
				FURNACE	.000	5.000	10.000
				WATER HEATER	.000	.000	3.000
				DUCTS IN UNCONDITIONED SPACE, NO TAPE	.000	.000	22.000

				FIREPLACE	6.000	12.000	54.000
				LEAKAGE AREA EQUALS THE SUM OF COLUMN “C” VALUES
				STEP 2: SELECT THE WINTER & SUMMER CFM/SQ. IN. FACTORS.
				WINTER CFM/SQ. IN. FACTOR			SUMMER CFM/SQ. IN. FACTOR
				NUMBER OF STORIES			NUMBER OF STORIES
				WIND EXPOSURE	1	2	3	1	2	3
				LESS THAN 30% EXPOSED WALL AREA	1.3	1.7	2	0.4	0.5	0.6
				30%-60% EXPOSED WALL AREA	1.6	2	2.3	0.6	0.7	0.8
				MORE THAN 60% EXPOSED WALL AREA	1.9	2.3	2.6	0.8	0.9	1
				WINTER CFM/SQ. IN. =			SUMMER CFM/SQ. IN. =
				STEP 3: CALCULATE THE INFILTRATIONS AC/HR FOR WINTER & SUMMER
				LEAKAGE AREA: SQ. IN.		INFILTRATION CFM	MIN. PER HR.	VOLUME CU. FT.		CRACK AC/HR
				WINTER =		X		60/		=
				SUMMER=		X		60/		=

## TABLE 6
TABLE 6
RATING AND SWING TEMPERATURE SWING MULTIPLIER (RSM)
METHOD USED TO SELECT EQUIPMENT	SUMMER DESIGN	TEMP SWING
SELECTION MADE AT THE ACTUAL SUMMER DESIGN CONDITION USING MANUFACTURER’S PERFORMANCE DATA		0.9	1
SELECTION MADE AT THE ARI STANDARD RATING DESIGN CONDITION	85-90	0.85	0.95
	95	0.9	1
	100	0.95	1.05
	105	1	1.1
	110	1.05	1.15
USE THIS TABLE WITH CALCULATION PROCEDURE D

## TABLE 7A
TABLE 7A
DUCT LOSS MULTIPLIERS
CASE 1- SUPPLY AIR TEMPERATURES BELOW 120°F	DUCT LOSS MULTIPLIERS
DUCT LOCATION AND INSULATION VALUE	WINTER DESIGN BELOW 15°F	WINTER DESIGN ABOVE 15°F
EXPOSED TO OUTDOOR AMBIENT
ATTIC, GARAGE, EXTERIOR WALL, OPEN CRAWLSPACE – NONE	0.3	0.25
ATTIC, GARAGE, EXTERIOR WALL, OPEN CRAWLSPACE (R2)	0.2	0.15
ATTIC, GARAGE, EXTERIOR WALL, OPEN CRAWLSPACE (R4)	0.15	0.1
ATTIC, GARAGE, EXTERIOR WALL, OPEN CRAWLSPACE (R6)	0.1	0.05
ENCLOSED IN AN UNHEATED SPACE
VENTED OR UNVENTED CRAWLSPACE OR BASEMENT – NONE	.20	.15
VENTED OR UNVENTED CRAWLSPACE OR BASEMENT (R2)	.15	.10
VENTED OR UNVENTED CRAWLSPACE OR BASEMENT (R4)	.10	.05
VENTED OR UNVENTED CRAWLSPACE OR BASEMENT (R6)	.05	.00
DUCT BURIED IN OR UNDER CONCRETE SLAB
NO EDGE INSULATION	.25	.20
EDGE INSULATION R VALUE = 3-4	.15	.10
EDGE INSULATION VALUE = 5-7	.10	.05
EDGE INSULATION VALUE = 7-9	.05	.00
CASE 1- SUPPLY AIR TEMPERATURES BELOW 120°F	WINTER DESIGN BELOW 15°F	WINTER DESIGN ABOVE 15°F
ATTIC, GARAGE, EXTERIOR WALL, OPEN CRAWLSPACE – NONE	.35	.30
ATTIC, GARAGE, EXTERIOR WALL, OPEN CRAWLSPACE (R2)	.25	.20
ATTIC, GARAGE, EXTERIOR WALL, OPEN CRAWLSPACE (R4)	.20	.15
ATTIC, GARAGE, EXTERIOR WALL, OPEN CRAWLSPACE (R6)	.15	.10
ENCLOSED IN AN UNHEATED SPACE
VENTED OR UNVENTED CRAWLSPACE OR BASEMENT – NONE	.25	.20
VENTED OR UNVENTED CRAWLSPACE OR BASEMENT (R2)	.20	.15
VENTED OR UNVENTED CRAWLSPACE OR BASEMENT (R4)	.15	.10
VENTED OR UNVENTED CRAWLSPACE OR BASEMENT (R6)	.10	.05
DUCT BURIED IN OR UNDER CONCRETE SLAB
NO EDGE INSULATION	.30	.25
EDGE INSULATION R VALUE = 3-4	.20	.15
EDGE INSULATION VALUE = 5-7	.15	.10
EDGE INSULATION VALUE = 7-9	.10	.05

## TABLE 7B
TABLE 7B
DUCT GAIN MULTIPLIERS
	DUCT GAIN MULTIPLIERS
DUCT LOCATION AND INSULATION VALUE
EXPOSED TO OUTDOOR AMBIENT
ATTIC, GARAGE, EXTERIOR WALL, OPEN CRAWLSPACE – NONE	0.30
ATTIC, GARAGE, EXTERIOR WALL, OPEN CRAWLSPACE (R2)	0.20
ATTIC, GARAGE, EXTERIOR WALL, OPEN CRAWLSPACE (R4)	0.15
ATTIC, GARAGE, EXTERIOR WALL, OPEN CRAWLSPACE (R6)	0.10
ENCLOSED IN AN UNHEATED SPACE
VENTED OR UNVENTED CRAWLSPACE OR BASEMENT – NONE	0.15
VENTED OR UNVENTED CRAWLSPACE OR BASEMENT (R2)	0.10
VENTED OR UNVENTED CRAWLSPACE OR BASEMENT (R4)	0.05
VENTED OR UNVENTED CRAWLSPACE OR BASEMENT (R6)	0.00
DUCT BURIED IN OR UNDER CONCRETE SLAB
NO EDGE INSULATION	0.10
EDGE INSULATION R VALUE = 3-4	0.05
EDGE INSULATION VALUE = 5-7	0.00
EDGE INSULATION VALUE = 7-9	0.00

## TABLE 9
1	GENERAL VENTILATION
	IF THE TABLE 5 SUMMER INFILTRATION CALCULATION INDICATES THAT THE SUMMER INFILTRATION RATE IS LESS THAN 0.35 AC/HR, MECHANICAL VENTILATION MAY BE REQUIRED. WHEN MECHANICAL VENTILATION IS INDICATED, PROVIDE 50 CFM OF OUTDOOR AIR OR THE QUANTITY OF OUTDOOR AIR CFM THAT IS INDICATED BY THE FOLLOWING FORMULA: (WHICHEVER IS GREATER).

	CFM =	(0.35- SUMMER AC/HR)/60		X	CU. FT. OF CONDITIONED SPACE

2	COMBUSTION AIR
	WHEN FOSSIL FUEL HEATING EQUIPMENT OBTAINS COMBUSTION AIR FROM WITHIN THE BUILDING ENVELOPE, THE TABLE 5 WINTER INFILTRATION CALCULATION SHOULD INDICATE THAT AT LEAST 0.50 CFM OF OUTDOOR AIR PER 1000 BTUH OF INPUT CAPACITY IS AVAILABLE FOR COMBUSTION AIR. IF THIS IS NOT THE CASE, MECHANICAL VENTILATION MAY BE REQUIRED. ALSO REFER TO SECTION 5 OF ANSI Z223.1/NFPA 54 – 1984

3	EXHAUST SYSTEMS
	RESIDENTIAL EXHAUST SYSTEMS ARE INTENDED TO OPERATE INTERMITTENTLY. THEREFORE, EACH EXHAUST SYSTEM SHOULD BE EQUIPPED WITH A READILY ACCESSIBLE SWITCH OR OTHER MEANS FOR SHUT OFF. DAMPERS SHOULD BE INSTALLED FOR THE PURPOSE OF ISOLATING EXHAUST OPENINGS WHEN THE EXHAUST FANS ARE NOT OPERATING. TYPICAL EXHAUST CFM FOR KITCHENS AND BATHS ARE:
	KITCHENS-	100 CFM		EACH BATH-		50 CFM

## Sheet19
GLASS			DOORS			EXTERIOR					ROOF					FLOOR
GLASS			DOORS			WOOD_CONST			WOOD_PART			BLOCK_PART			BLOCK_CONST			LIGHT_ROOF			DARK_ROOF			FLOOR
NO. 1 SINGLE PANE WINDOW CLEAR GLASS	A.	WOOD FRAME	NO. 10 WOOD DOORS	A. HOLLOW CORE		NO. 12 WOOD FRAME EXTERIOR WALLS WITH SHEATHING AND SIDING OR BRICK VENEER OR OTHER EXTERIOR FINISH	A. NONE ½” GYPSUM BOARD (R0.5)		NO. 13 PARTITIONS BETWEEN CONDITIONED AND UNCONDITIONED SPACE – WOOD FRAME PARTITIONS	A.	NONE ½” GYPSUM BOARD (R0.5)	NO. 13.1 PARTITIONS BETWEEN CONDITIONED & UNCONDITIONED SPACE. BRICK OR BLOCK PARTITIONS A. 8” OR 12” BLOCK, NO INSUL., UNFINISHED			NO. 14 MASONRY WALLS, BLOCK OR BRICK FINISHED OR UNFINISHED – ABOVE GRADE	A.	8” OR 12” BLOCK, NO INSUL., UNFINISHED	NO. 16 CEILINGS UNDER A VENTILATED ATTIC (LIGHT COLORED ROOF)	A.	NO INSULATION	NO. 16 CEILINGS UNDER A VENTILATED ATTIC (DARK COLORED ROOF)	A.	NO INSULATION	NO. 19 FLOORS OVER A BASEMENT OR ENCLOSED CRAWL SPACE	A.	HARDWOOD FLOOR, NO INSULATION
NO. 1 SINGLE PANE WINDOW CLEAR GLASS	B.	T.I.M. FRAME	NO. 10 WOOD DOORS	B. HOLLOW CORE & WOOD STORM		NO. 12 WOOD FRAME EXTERIOR WALLS WITH SHEATHING AND SIDING OR BRICK VENEER OR OTHER EXTERIOR FINISH	B. NONE ½” ASPHAULT BOARD (R1.3)		NO. 13 PARTITIONS BETWEEN CONDITIONED AND UNCONDITIONED SPACE – WOOD FRAME PARTITIONS	B.	NONE ½” ASPHAULT BOARD (R1.3)	NO. 13.1 PARTITIONS BETWEEN CONDITIONED & UNCONDITIONED SPACE. BRICK OR BLOCK PARTITIONS B. 8” OR 12” BLOCK + R5				B.	8” OR 12” BLOCK + R5		B.	R7 INSULATION		B.	R7 INSULATION		B.	HARDWOOD FLOOR (R11)
NO. 1 SINGLE PANE WINDOW CLEAR GLASS	C.	METAL FRAME	NO. 10 WOOD DOORS	C. HOLLOW CORE & METAL STORM		NO. 12 WOOD FRAME EXTERIOR WALLS WITH SHEATHING AND SIDING OR BRICK VENEER OR OTHER EXTERIOR FINISH	C. R11 ½” GYPSUM BOARD (R0.5)		NO. 13 PARTITIONS BETWEEN CONDITIONED AND UNCONDITIONED SPACE – WOOD FRAME PARTITIONS	C.	R11 ½” GYPSUM BOARD (R0.5)	NO. 13.1 PARTITIONS BETWEEN CONDITIONED & UNCONDITIONED SPACE. BRICK OR BLOCK PARTITIONS C. 8” OR 12” BLOCK + R11				C.	8” OR 12” BLOCK + R11		C.	R11 INSULATION		C.	R11 INSULATION		C.	HARDWOOD FLOOR (R13)
NO. 1 SINGLE PANE WINDOW LOW EMITTANCE GLASS, E = 0.60	D.	WOOD FRAME	NO. 10 WOOD DOORS	D. SOLID CORE		NO. 12 WOOD FRAME EXTERIOR WALLS WITH SHEATHING AND SIDING OR BRICK VENEER OR OTHER EXTERIOR FINISH	D	R11 ½” ASPHAULT BOARD (R1.3)	NO. 13 PARTITIONS BETWEEN CONDITIONED AND UNCONDITIONED SPACE – WOOD FRAME PARTITIONS	D.	R11 ½” ASPHAULT BOARD (R1.3)	NO. 13.1 PARTITIONS BETWEEN CONDITIONED & UNCONDITIONED SPACE. BRICK OR BLOCK PARTITIONS D. 8” OR 12” BLOCK + R19				D.	8” OR 12” BLOCK + R19		D.	R19 INSULATION		D.	R19 INSULATION		D.	HARDWOOD FLOOR (R19)
NO. 1 SINGLE PANE WINDOW LOW EMITTANCE GLASS, E = 0.60	E.	T.I.M. FRAME	NO. 10 WOOD DOORS	E. SOLID CORE & WOOD STORM		NO. 12 WOOD FRAME EXTERIOR WALLS WITH SHEATHING AND SIDING OR BRICK VENEER OR OTHER EXTERIOR FINISH	D	R11 ½” BEAD BOARD (R1.8)	NO. 13 PARTITIONS BETWEEN CONDITIONED AND UNCONDITIONED SPACE – WOOD FRAME PARTITIONS		R11 ½” BEAD BOARD (R1.8)	NO. 13.1 PARTITIONS BETWEEN CONDITIONED & UNCONDITIONED SPACE. BRICK OR BLOCK PARTITIONS E. 4” BRICK, 8” BLOCK, NO INSUL				E.	4” BRICK, 8” BLOCK, NO INSUL		E.	R22 INSULATION		E.	R22 INSULATION		E.	HARDWOOD FLOOR (R30)
NO. 1 SINGLE PANE WINDOW LOW EMITTANCE GLASS, E = 0.60	F.	METAL FRAME	NO. 10 WOOD DOORS	F. SOLID CORE & METAL STORM		NO. 12 WOOD FRAME EXTERIOR WALLS WITH SHEATHING AND SIDING OR BRICK VENEER OR OTHER EXTERIOR FINISH	D	R13 ½” GYPSUM BOARD (R0.5)	NO. 13 PARTITIONS BETWEEN CONDITIONED AND UNCONDITIONED SPACE – WOOD FRAME PARTITIONS		R13 ½” GYPSUM BOARD (R0.5)	NO. 13.1 PARTITIONS BETWEEN CONDITIONED & UNCONDITIONED SPACE. BRICK OR BLOCK PARTITIONS F. 4” BRICK, 8” BLOCK + R5				F.	4” BRICK, 8” BLOCK + R5		F.	R26 INSULATION		F.	R26 INMSULATION		F.	CARPET FLOOR NO INSULATION
NO. 1 SINGLE PANE WINDOW LOW EMITTANCE GLASS, E = 0.40	G.	WOOD FRAME	NO. 10 WOOD DOORS	G. PANEL		NO. 12 WOOD FRAME EXTERIOR WALLS WITH SHEATHING AND SIDING OR BRICK VENEER OR OTHER EXTERIOR FINISH	E.	R11 ½” POLY BOARD(R2.5)	NO. 13 PARTITIONS BETWEEN CONDITIONED AND UNCONDITIONED SPACE – WOOD FRAME PARTITIONS	E.	R11 ½” POLY BOARD(R2.5)	NO. 13.1 PARTITIONS BETWEEN CONDITIONED & UNCONDITIONED SPACE. BRICK OR BLOCK PARTITIONS G. 4” BRICK, 8” BLOCK + R11				G.	4” BRICK, 8” BLOCK + R11		G.	R30 INSULATION		G.	R30 INSULATION		G.	CARPET FLOOR (R11)
NO. 1 SINGLE PANE WINDOW LOW EMITTANCE GLASS, E = 0.40	H.	T.I.M. FRAME	NO. 10 WOOD DOORS	H. PANEL & WOOD STORM		NO. 12 WOOD FRAME EXTERIOR WALLS WITH SHEATHING AND SIDING OR BRICK VENEER OR OTHER EXTERIOR FINISH		R11 ¾” EXTR POLYBOARD (R2.5)	NO. 13 PARTITIONS BETWEEN CONDITIONED AND UNCONDITIONED SPACE – WOOD FRAME PARTITIONS	E.	R11 ¾” EXTR POLYBOARD (R2.5)	NO. 13.1 PARTITIONS BETWEEN CONDITIONED & UNCONDITIONED SPACE. BRICK OR BLOCK PARTITIONS H. 4” BRICK, 8” BLOCK + R19				H.	4” BRICK, 8” BLOCK + R19		H.	R38 INSULATION		H.	R38 INSULATION		H.	CARPET FLOOR (R13)
NO. 1 SINGLE PANE WINDOW LOW EMITTANCE GLASS, E = 0.40	I.	METAL FRAME	NO. 10 WOOD DOORS	I. PANEL & METAL STORM		NO. 12 WOOD FRAME EXTERIOR WALLS WITH SHEATHING AND SIDING OR BRICK VENEER OR OTHER EXTERIOR FINISH		R13 ½” ASPHALT BOARD (R1.3)	NO. 13 PARTITIONS BETWEEN CONDITIONED AND UNCONDITIONED SPACE – WOOD FRAME PARTITIONS	E.	R13 ½” ASPHALT BOARD (R1.3)				NO. 15 MASONRY WALLS, BLOCK OR BRICK, FINISHED OR UNFINISHED – WALLS EXTEND 2’-5’ BELOW GRADE	A.	8” OR 12” BLOCK + NO INSUL.		I.	R44 INSULATION		I.	R44 INSULATION		I.	CARPET FLOOR (R19)
NO. 1 SINGLE PANE WINDOW LOW EMITTANCE GLASS, E = 0.20	J.	WOOD FRAME	NO. 11 METAL DOORS	A. FIBERGLASS CORE		NO. 12 WOOD FRAME EXTERIOR WALLS WITH SHEATHING AND SIDING OR BRICK VENEER OR OTHER EXTERIOR FINISH		R13 R13 ½” BEAD BOARD (R1.8)	NO. 13 PARTITIONS BETWEEN CONDITIONED AND UNCONDITIONED SPACE – WOOD FRAME PARTITIONS	E.	R13 R13 ½” BEAD BOARD (R1.8)					B.	8” OR 12” BLOCK + R5		J.	R57 INSULATION		J.	R57 INSULATION		J.	CARPET FLOOR (R30)
NO. 1 SINGLE PANE WINDOW LOW EMITTANCE GLASS, E = 0.20	K.	T.I.M. FRAME	NO. 11 METAL DOORS	B. FIBERGLASS CORE & STORM		NO. 12 WOOD FRAME EXTERIOR WALLS WITH SHEATHING AND SIDING OR BRICK VENEER OR OTHER EXTERIOR FINISH	F.	R11 1” BEAD BOARD (R3.6)	NO. 13 PARTITIONS BETWEEN CONDITIONED AND UNCONDITIONED SPACE – WOOD FRAME PARTITIONS	F.	R11 1” BEAD BOARD (R3.6)					C.	8” OR 12” BLOCK + R11		K.	WOOD DECKING, NO INSULATION		K.	WOOD DECKING, NO INSULATION	NO. 20 FLOORS OVER AN OPEN CRAWL SPACE OR GARAGE	A.	HARDWOOD FLOOR, NO INSULATION
NO. 1 SINGLE PANE WINDOW LOW EMITTANCE GLASS, E = 0.20	L.	METAL FRAME	NO. 11 METAL DOORS	C. POLYSTYRENE CORE		NO. 12 WOOD FRAME EXTERIOR WALLS WITH SHEATHING AND SIDING OR BRICK VENEER OR OTHER EXTERIOR FINISH		R11 ¾” EXTR POLY BOARD (R3.8)	NO. 13 PARTITIONS BETWEEN CONDITIONED AND UNCONDITIONED SPACE – WOOD FRAME PARTITIONS	F.	R11 ¾” EXTR POLY BOARD (R3.8)					D.	8” OR 12” BLOCK + R19	NO. 17 ROOF ON EXPOSED BEAM OR RAFTERS (LIGHT COLORED ROOF)	A.	1 ½” WOOD DECKING, NO INSULATION	NO. 17. ROOF ON EXPOSED BEAM OR RAFTERS (DARK COLORED ROOF)	A.	1 ½” WOOD DECKING, NO INSULATION		B.	HARDWOOD FLOOR (R11)
NO. 2 SINGLE PANE WINDOW & STORM CLEAR GLASS	A.	WOOD FRAME	NO. 11 METAL DOORS	D. POLYSTYRENE CORE & STORM		NO. 12 WOOD FRAME EXTERIOR WALLS WITH SHEATHING AND SIDING OR BRICK VENEER OR OTHER EXTERIOR FINISH		R13 ½” EXTR POLY BOARD (R2.5)	NO. 13 PARTITIONS BETWEEN CONDITIONED AND UNCONDITIONED SPACE – WOOD FRAME PARTITIONS	F.	R13 ½” EXTR POLY BOARD (R2.5)				NO. 15 MASONRY WALLS, BLOCK OR BRICK, FINISHED OR UNFINISHED – WALLS EXTEND MORE THAN 5’ BELOW GRADE	E.	4” BRICK+ 8” BLOCK, NO INSUL.		B.	1 ½” WOOD DECKING (R4)		B.	1 ½” WOOD DECKING (R4)		C.	HARDWOOD FLOOR (R13)
NO. 2 SINGLE PANE WINDOW & STORM CLEAR GLASS	B.	T.I.M. FRAME	NO. 11 METAL DOORS	E. URETHANE CORE		NO. 12 WOOD FRAME EXTERIOR WALLS WITH SHEATHING AND SIDING OR BRICK VENEER OR OTHER EXTERIOR FINISH		R13 ¾” BEAD BOARD (R2.7)	NO. 13 PARTITIONS BETWEEN CONDITIONED AND UNCONDITIONED SPACE – WOOD FRAME PARTITIONS	F.	R13 ¾” BEAD BOARD (R2.7)					F.	4” BRICK+ 8” BLOCK + R5		C.	1 ½” WOOD DECKING (R5)		C.	1 ½” WOOD DECKING (R5)		D.	HARDWOOD FLOOR (R19)
NO. 2 SINGLE PANE WINDOW & STORM CLEAR GLASS	C.	METAL FRAME	NO. 11 METAL DOORS	F. URETHANE CORE & STORM		NO. 12 WOOD FRAME EXTERIOR WALLS WITH SHEATHING AND SIDING OR BRICK VENEER OR OTHER EXTERIOR FINISH	G.	R13 ¾” EXTR POLY BOARD (R3.8)	NO. 13 PARTITIONS BETWEEN CONDITIONED AND UNCONDITIONED SPACE – WOOD FRAME PARTITIONS	G.	R13 ¾” EXTR POLY BOARD (R3.8)					G.	4” BRICK+ 8” BLOCK + R11		D.	1 ½” WOOD DECKING (R6)		D.	1 ½” WOOD DECKING (R6)		E.	HARDWOOD FLOOR (R30)
NO. 2 SINGLE PANE WINDOW & STORM LOW EMITTANCE GLASS	D.	WOOD FRAME				NO. 12 WOOD FRAME EXTERIOR WALLS WITH SHEATHING AND SIDING OR BRICK VENEER OR OTHER EXTERIOR FINISH		R13 1” BEAD BOARD (R3.6)	NO. 13 PARTITIONS BETWEEN CONDITIONED AND UNCONDITIONED SPACE – WOOD FRAME PARTITIONS	G.	R13 1” BEAD BOARD (R3.6)					H.	4” BRICK+ 8” BLOCK + R19		E.	1 ½” WOOD DECKING (R8)		E.	1 ½” WOOD DECKING (R8)		F.	CARPET FLOOR NO INSULATION
NO. 2 SINGLE PANE WINDOW & STORM LOW EMITTANCE GLASS	E.	T.I.M. FRAME				NO. 12 WOOD FRAME EXTERIOR WALLS WITH SHEATHING AND SIDING OR BRICK VENEER OR OTHER EXTERIOR FINISH	H.	R11 1” EXTR POLY BOARD (R5.0)	NO. 13 PARTITIONS BETWEEN CONDITIONED AND UNCONDITIONED SPACE – WOOD FRAME PARTITIONS	H.	R11 1” EXTR POLY BOARD (R5.0)					F.	2” SHREDDED WOOD PLANKS		F.	2” SHREDDED WOOD PLANKS		G.	CARPET FLOOR (R11)
NO. 2 SINGLE PANE WINDOW & STORM LOW EMITTANCE GLASS	F.	METAL FRAME				NO. 12 WOOD FRAME EXTERIOR WALLS WITH SHEATHING AND SIDING OR BRICK VENEER OR OTHER EXTERIOR FINISH		R13 1” EXTR POLY BOARD (R5.0)	NO. 13 PARTITIONS BETWEEN CONDITIONED AND UNCONDITIONED SPACE – WOOD FRAME PARTITIONS	H.	R13 1” EXTR POLY BOARD (R5.0)					G.	3” SHREDDED WOOD PLANKS		G.	3” SHREDDED WOOD PLANKS		H.	CARPET FLOOR (R13)
NO. 3 DOUBLE PANE WINDOW CLEAR GLASS	A.	WOOD FRAME				NO. 12 WOOD FRAME EXTERIOR WALLS WITH SHEATHING AND SIDING OR BRICK VENEER OR OTHER EXTERIOR FINISH		R19 ½” GYPSUM BOARD (R0.5)	NO. 13 PARTITIONS BETWEEN CONDITIONED AND UNCONDITIONED SPACE – WOOD FRAME PARTITIONS	H.	R19 ½” GYPSUM BOARD (R0.5)					H.	1 ½” FIBER BOARD INSUL		H.	1 ½” FIBER BOARD INSUL		I.	CARPET FLOOR (R19)
NO. 3 DOUBLE PANE WINDOW CLEAR GLASS	B.	T.I.M. FRAME				NO. 12 WOOD FRAME EXTERIOR WALLS WITH SHEATHING AND SIDING OR BRICK VENEER OR OTHER EXTERIOR FINISH	I.	R19 ½” ASPHALT BOARD (R1.3)	NO. 13 PARTITIONS BETWEEN CONDITIONED AND UNCONDITIONED SPACE – WOOD FRAME PARTITIONS	I.	R19 ½” ASPHALT BOARD (R1.3)					I.	2” FIBER BOARD INSUL		I.	2” FIBER BOARD INSUL		J.	CARPET FLOOR (R30)
NO. 3 DOUBLE PANE WINDOW CLEAR GLASS	C.	METAL FRAME				NO. 12 WOOD FRAME EXTERIOR WALLS WITH SHEATHING AND SIDING OR BRICK VENEER OR OTHER EXTERIOR FINISH		R19 ½” BEAD BOARD (R1.8)	NO. 13 PARTITIONS BETWEEN CONDITIONED AND UNCONDITIONED SPACE – WOOD FRAME PARTITIONS	I.	R19 ½” BEAD BOARD (R1.8)					J.	3” FIBER BOARD INSUL		J.	3” FIBER BOARD INSUL	NO. 21 BASEMENT FLOORS	A.	2 OR MORE FEET BELOW GRADE
NO. 3 DOUBLE PANE WINDOW LOW EMITTANCE GLASS	D.	WOOD FRAME				NO. 12 WOOD FRAME EXTERIOR WALLS WITH SHEATHING AND SIDING OR BRICK VENEER OR OTHER EXTERIOR FINISH	J.	R11 R8 SHEATHING	NO. 13 PARTITIONS BETWEEN CONDITIONED AND UNCONDITIONED SPACE – WOOD FRAME PARTITIONS	J.	R11 R8 SHEATHING					K.	1 ½” WOOD DECKING (R13)		K.	1 ½” WOOD DECKING (R13)	NO. 22 CONCRETE SLAB ON GRADE	A.	NO EDGE INSULATION
NO. 3 DOUBLE PANE WINDOW LOW EMITTANCE GLASS	E.	T.I.M. FRAME				NO. 12 WOOD FRAME EXTERIOR WALLS WITH SHEATHING AND SIDING OR BRICK VENEER OR OTHER EXTERIOR FINISH		R13 R8 SHEATHING	NO. 13 PARTITIONS BETWEEN CONDITIONED AND UNCONDITIONED SPACE – WOOD FRAME PARTITIONS	J.	R13 R8 SHEATHING					L.	1 ½” WOOD DECKING (R19)		L.	1 ½” WOOD DECKING (R19)		B.	1” EDGE INSULATION (R5)
NO. 3 DOUBLE PANE WINDOW LOW EMITTANCE GLASS	F.	METAL FRAME				NO. 12 WOOD FRAME EXTERIOR WALLS WITH SHEATHING AND SIDING OR BRICK VENEER OR OTHER EXTERIOR FINISH		R19 ½” OR ¾” EXTR POLY BOARD	NO. 13 PARTITIONS BETWEEN CONDITIONED AND UNCONDITIONED SPACE – WOOD FRAME PARTITIONS	J.	R19 ½” OR ¾” EXTR POLY BOARD					NO. 18 ROOF CEILING COMBINATION (LIGHT COLORED ROOF)	A.	NO INSULATION	NO. 18 ROOF CEILING COMBINATION (DARK COLORED ROOF)	A.	NO INSULATION		C.	1 ½” EDGE INSULATION (R8)
NO. 3 DOUBLE PANE WINDOW ADJUSTABLE BLIND BETWEEN PANES	G.	WOOD FRAME				NO. 12 WOOD FRAME EXTERIOR WALLS WITH SHEATHING AND SIDING OR BRICK VENEER OR OTHER EXTERIOR FINISH		R19 ¾” OR 1’ BEAD BOARD	NO. 13 PARTITIONS BETWEEN CONDITIONED AND UNCONDITIONED SPACE – WOOD FRAME PARTITIONS	J.	R19 ¾” OR 1’ BEAD BOARD					B.	R11 BATTS		B.	R11 BATTS		D.	2” EDGE INSULATION (R11)
NO. 3 DOUBLE PANE WINDOW ADJUSTABLE BLIND BETWEEN PANES	H.	T.I.M. FRAME				NO. 12 WOOD FRAME EXTERIOR WALLS WITH SHEATHING AND SIDING OR BRICK VENEER OR OTHER EXTERIOR FINISH	K.	R19 1” EXTR POLY BOARD (R5.0)	NO. 13 PARTITIONS BETWEEN CONDITIONED AND UNCONDITIONED SPACE – WOOD FRAME PARTITIONS	K.	R19 1” EXTR POLY BOARD (R5.0)					C.	R19 BATTS		C.	R19 BATTS	NO. 23 CONCRETE SLAB WITH PERIMETER WARM AIR DUCT SYSTEM	A.	NO EDGE INSULATION
NO. 4 DOUBLE PANE WINDOW & STORM CLEAR GLASS	A.	WOOD FRAME				NO. 12 WOOD FRAME EXTERIOR WALLS WITH SHEATHING AND SIDING OR BRICK VENEER OR OTHER EXTERIOR FINISH	L.	R19 R8 SHEATHING	NO. 13 PARTITIONS BETWEEN CONDITIONED AND UNCONDITIONED SPACE – WOOD FRAME PARTITIONS	L.	R19 R8 SHEATHING					D.	R22 BATTS (2” X 8” RAFTERS)		D.	R22 BATTS (2” X 8” RAFTERS)		B.	1” EDGE INSULATION (R5)
	B.	T.I.M. FRAME					E.	R26 BATTS (2” X 8” RAFTERS)		E.	R26 BATTS (2” X 8” RAFTERS)		C.	1 ½” EDGE INSULATION (R8)
	C.	METAL FRAME					F.	R30 BATTS (2” X 10” RAFTERS)		F.	R30 BATTS (2” X 10” RAFTERS)		D.	2” EDGE INSULATION (R11)
NO. 4 DOUBLE PANE WINDOW & STORM LOW EMITTANCE GLASS	D.	WOOD FRAME
	E.	T.I.M. FRAME
	F.	METAL FRAME
NO. 5 TRIPLE PANE WINDOWS CLEAR GLASS	A.	WOOD FRAME
	B.	T.I.M. FRAME
	C.	METAL FRAME
NO. 5 TRIPLE PANE WINDOWS LOW EMITTANCE GLASS	D.	WOOD FRAME
	E.	T.I.M. FRAME
	F.	METAL FRAME
NO. 5 TRIPLE PANE WINDOWS CLEAR GLASS & STORM	G.	WOOD FRAME
	H.	T.I.M. FRAME
	I.	METAL FRAME
NO. 6 JALOUSIE WINDOWS JALOUSIE WINDOWS	A.	METAL FRAME-SINGLE GLASS
	B.	METAL FRAME-SINGLE GLASS & STORM
NO. 7 SKYLIGHTS SINGLE; CLEAR GLASS	A.	WOOD FRAME
	B.	T.I.M. FRAME
	C.	METAL FRAME
NO. 7 SKYLIGHTS SINGLE; PLASTIC DOME	D.	WOOD FRAME
	E.	T.I.M. FRAME
	F.	METAL FRAME
NO. 7 SKYLIGHTS DOUBLE; PLASTIC DOME OR CLEAR GLASS	G.	WOOD FRAME
	H.	T.I.M. FRAME
	I.	METAL FRAME
NO. 7 SKYLIGHTS DOUBLE; LOW EMITTANCE GLASS	J.	WOOD FRAME
	K.	T.I.M. FRAME
	L.	METAL FRAME
NO. 8 SLIDING GLASS DOORS SINGLE PANE; CLEAR GLASS	A.	WOOD FRAME
	B.	T.I.M. FRAME
	C.	METAL FRAME
NO. 8 SLIDING GLASS DOORS SINGLE PANE LOW E GLASS	D.	WOOD FRAME
	E.	T.I.M. FRAME
	F.	METAL FRAME
NO. 8 SLIDING GLASS DOORS SINGLE PANE & STORM, CLEAR GLASS	G.	WOOD FRAME
	H.	T.I.M. FRAME
	I.	METAL FRAME
NO. 8 SLIDING GLASS DOORS SINGLE PANE & STORM, LOW E GLASS	J.	WOOD FRAME
	K.	T.I.M. FRAME
	L.	METAL FRAME
NO. 8 SLIDING GLASS DOORS DOUBLE PANE, CLEAR GLASS	M.	WOOD FRAME
	N.	T.I.M. FRAME
	O.	METAL FRAME
NO. 8 SLIDING GLASS DOORS DOUBLE PANE, LOW E GLASS	P.	WOOD FRAME
	Q.	T.I.M. FRAME
	R.	METAL FRAME
NO. 8 SLIDING GLASS DOORS TRIPLE PANE OR DOUBLE PANE & STORM	S.	WOOD FRAME
	T.	T.I.M. FRAME
	U.	METAL FRAME
NO. 8 SLIDING GLASS DOORS TRIPLE OR DOUBLE & STORM ,LOW E	V.	WOOD FRAME
	W.	T.I.M. FRAME
	X.	METAL FRAME
NO. 9 FRENCH DOORS SINGLE PANE, CLEAR GLASS	A.	WOOD FRAME
	B.	T.I.M. FRAME
	C.	METAL FRAME
NO. 9 FRENCH DOORS SINGLE PANE, LOW E GLASS	D.	WOOD FRAME
	E.	T.I.M. FRAME
	F.	METAL FRAME
NO. 9 FRENCH DOORS SINGLE PANE & STORM, CLEAR GLASS	G.	WOOD FRAME
	H.	T.I.M. FRAME
	I.	METAL FRAME
NO. 9 FRENCH DOORS DOUBLE PANE, CLEAR GLASS	M.	WOOD FRAME
	N.	T.I.M. FRAME
	O.	METAL FRAME
NO. 9 FRENCH DOORS DOUBLE PANE, LOW E GLASS	P.	WOOD FRAME
	Q.	T.I.M. FRAME
	R.	METAL FRAME
NO. 9 FRENCH DOORS TRIPLE PANE, CLEAR GLASS	S.	WOOD FRAME
	T.	T.I.M. FRAME
	U.	METAL FRAME
NO. 9 FRENCH DOORS TRIPLE PANE, LOW E	V.	WOOD FRAME
	W.	T.I.M. FRAME
	X.	METAL FRAME